Macquarie Coal Complex Transformation Precinct

Site-Level Enhancement Plan, Statutory Due Diligence & Technical Studies Digest

| Document Reference | AURA-SITE-LMCC-20260907-V2.4 |
| --- | --- |
| Target Audience | Planning Authorities (NSW DPHI/IPC), Clean Energy Consortiums, Land Developers |
| Key Metrics | 320 ha Gross Site Area ¦ 44.5 ha Net Developable Pads ¦ 500 MVA Substation ¦ 49 MWh Void PHES |
| Statutory Base | Synthesis of 15 Public Exhibition Technical Documents (>135 MB) |
| Interactive WebGIS | https://aura.getback2basics.net/projects/index_LMCC_MacquarieCoal.html |
| Source Materials | docs/business/macquarie_coal_precinct_site_enhancement_plan.md ¦ docs/archive/macquarie_coal_precinct_docs/*.md |

STATUTORY SITE EVALUATION SUMMARY A rigorous statutory-grade site evaluation demonstrating AURA's forensic siting capability. Topologically extracts 10 Net Developable Pads (NDPs) from raw brownfield mining land, integrating 1% AEP flood modeling, geotechnical mine subsidence strain zones (G1–G3), 330kV transmission injection headroom, and closed-loop thermodynamic cooling.

# Visual Portfolio & Interactive System Captures

Figure 1: Macquarie Coal Complex Site-Level 3D WebGIS showing 10 developable pads and hazard setbacks.

Figure 2: Forensic statutory planning report evaluating power headroom and flood constraints.

Figure 3: Master site enhancement strategy transforming mining land into a green compute hub.

# Macquarie Coal Complex Transformation Precinct: Site-Level Enhancement Plan

Comprehensive Review of Public Exhibition Technical Studies & Geospatial Siting Blueprint

Author: George Chandeep Corea (Geospatial Data Lead, *GetBack2Basics* | Project Lead, *AURA Siting Crafter*)

Context: Review and Master Plan Enhancement for NSW Department of Planning, Housing and Infrastructure (DPHI), Lake Macquarie City Council, Net Zero Economy Authority (NZEA), and Glencore

Reference Case: Planning Proposal PPR-Macquarie Coal Complex Transformation Precinct (Post-Exhibition July/August 2026)

Date: September 2026

Interactive Geospatial Viewer: https://storage.googleapis.com/aura-siting-crafter-geolibre-app/index.html

---

## 1. Executive Summary & Document Review Synthesis

The public exhibition of the Macquarie Coal Complex Transformation Precinct Master Plan and Explanation of Intended Effects (EIE) represents a landmark post-mining transition initiative in New South Wales. Encompassing over 1,100 hectares of former coal mining land across four historic operations (West Wallsend Colliery, Macquarie Coal Preparation Plant [MCPP], Westside Mine, and Teralba Colliery Northgate/Southgate), the precinct is slated to unlock ~500 hectares of E4 General Industrial land and generate 1,130+ direct jobs.

A rigorous, multi-disciplinary review of all 15 statutory exhibition documents and technical assessments (prepared by Aurecon Australasia for DPHI and Council) confirms the immense strategic potential of the site, but also highlights critical site-level friction points:

Gross vs. Net Developable Area Ambiguity: Gross ~500 ha zoning figures mask significant constructability deductions (unconsolidated Tailings Storage Facility [TSF], slope gradients >5%, riparian setbacks, dam break zones, and mine subsidence overlays).

Infrastructure Servicing Gaps: Power transmission (330kV / 132kV) is adjacent but lacks a dedicated multi-user terminal substation strategy; water and sewer networks require capital extensions; telecommunications relies entirely on developer-led piecemeal delivery.

Underutilized Strategic Assets: The existing 1.8 km heavy rail loop and siding and the grade-separated internal mine haul road are not fully optimized as primary catalysts for regional intermodal freight and community-bypassing arterial movement.

Energy & Water Circularity Deficits: Current plans do not mandate non-potable closed-loop industrial cooling or capitalize on the unique 120m hydraulic head between the upper ridgeline and the Westside open-cut void for pumped hydro energy storage (PHES).

This Site-Level Enhancement Plan delivers an evidence-based, geospatial blueprint to resolve these constraints, accelerate development approvals, and elevate the precinct into Australia's premier green-industrial and sovereign digital infrastructure hub.

---

## 2. Technical Studies Review Matrix (All 15 Exhibition Documents)

| Document | Page Count | Key Baseline Findings & Constraints | Site-Level Enhancement Opportunity |
| --- | --- | --- | --- |
| **1. Master Plan** | 60 | Establishes 4 sub-precincts (MCPP/TSF, Westside, Teralba North, Teralba Southgate); envisions high-tech industrial, clean energy, and open space. | Transition from broad zoning to **10 shovel-ready, geotechnical-certified Net Developable Pads (NDPs)** with explicit staging. |
| **2. EIE (Rezoning)** | 25 | Rezones land to E4 General Industrial, C2 Conservation, and SP2 Infrastructure under Lake Macquarie LEP 2014 & Regional Precincts SEPP. | Embed site-specific DCP clauses for **500m acoustic buffers, closed-loop cooling mandates, and expedited Subsidence Advisory protocols**. |
| **3. Utilities Engineering** | 74 | Adjacent Transgrid 330kV and Ausgrid 132kV lines; 375mm Hunter Water potable main along Cessnock Rd; developer-led NBN pit & pipe. | Master plan a **central 200–500 MVA multi-user substation hub** and a **dual-pipe tertiary-treated recycled water network**. |
| **4. Geotechnical Report** | 106 | Shallow/deep workings in Great Northern, Fassifern, Young Wallsend seams; soft alluvium in north; unconsolidated TSF; slope instability. | Establish a **Pre-Approved Foundation Matrix (raft slabs, void grouting, pile criteria)** pre-cleared with Subsidence Advisory NSW. |
| **5. Contamination Assessment** | 66 | Hydrocarbon hotspots around former workshops/washbays; low-moderate acid mine drainage risk; ongoing TSF consolidation. | Deploy **insitu bioremediation for hydrocarbons, alkaline buffering blankets for reject, and staged TSF capping**. |
| **6. Dam Engineering Report** | 28 | TSF is a Declared Dam under Dams Safety NSW; Consequence Category requires dam break inundation buffers and ongoing surveillance. | Implement a **3-Phase TSF Decommissioning & Wick-Drain Dewatering Program** to transition land from exclusion to solar/BESS pads. |
| **7. Flooding & Water Cycle** | 92 | 1% AEP flood affects northern Cockle/Diega Creek flats; 10m–40m riparian buffers; NorBE stormwater treatment targets. | Integrate **regional multi-functional bioretention basins, constructed treatment wetlands, and flood conveyance corridors**. |
| **8. Economics & Market** | 115 | Target sectors: advanced manufacturing, clean energy, digital infrastructure, circular economy, freight logistics; 1,130 direct jobs. | Target **high-power-density hyperscale AI data centres and advanced clean manufacturing** to triple job density per hectare. |
| **9. Traffic & Transport** | 87 | Access via Cessnock Rd, Wilton Rd, Wakefield Rd; freight trip generation; disused rail loop and private haul road. | Formalize the **internal Haul Road as a heavy-freight public spine** and **reactivate the 1.8km Rail Siding as an Intermodal Terminal**. |
| **10. Biodiversity Assessment** | 174 | Spotted Gum Ironbark Forest, Swamp Sclerophyll EEC; Koala habitat corridors across Sugarloaf Range; Biodiversity Offset Scheme. | Establish a **connected 250m-wide Sugarloaf-to-Awaba Biodiversity Bio-Link** in the C2 zone with dedicated fauna overpasses. |
| **11. Bush Fire Assessment** | 35 | High bushfire hazard (Category 1 vegetation); FFDI 100 / FDI 80; requires 20m–45m Asset Protection Zones (APZs). | Embed **perimeter ring-roads doubling as dual-purpose APZs and emergency egress routes** under PBF 2019. |
| **12. Noise & Vibration** | 37 | Low night-time RBL (30–35 dBA); sensitive receivers in Barnsley, Teralba, Wakefield; night PNTL 35 dBA. | Sculpt **6m–8m landscaped acoustic earthen bunds** along eastern/northeastern boundaries for 24/7 industrial operations. |
| **13. Air Quality & Odour** | 41 | PM10/PM2.5 baseline compliant post-mining; low industrial odour risk; dust management required during civil earthworks. | Standardize **real-time PM10/PM2.5 IoT boundary monitoring** and progressive revegetation during civil works. |
| **14. Evaluation Panel Report** | 2 | Endorses State Significant Rezoning pathway; highlights need for coordinated infrastructure delivery and clear staging. | Establish a **Precinct Infrastructure Delivery Authority / Special Infrastructure Contribution (SIC)** mechanism. |
| **15. Community FAQs** | 5 | Addresses public feedback regarding heavy traffic, community amenity, environmental preservation, and job creation. | Deliver transparent, open-access **Digital Twin & WebGIS inspection tools** to maintain high community trust. |

---

## 3. The 6-Pillar Site-Level Enhancement Blueprint

flowchart TD
    subgraph P1["Pillar 1: Precision Net Developable Area (NDA)"]
        A1["Gross Footprint: ~1,100 ha"] --> A2["Deductions: Slopes, Riparian, TSF, Easements"]
        A2 --> A3["10 Geotechnical-Certified Net Developable Pads: 185 - 320 ha"]
    end

    subgraph P2["Pillar 2: Sovereign Utility and Circular Energy Hub"]
        B1["Transgrid 330kV Corridor"] --> B2["Multi-User 330/132kV Terminal Substation Pad: 200-500 MVA"]
        B2 --> B3["100MW/400MWh BESS + 49 MWh Pit Void Closed-Loop Pumped Hydro"]
        B4["Hunter Water WWTW"] --> B5["Dual-Pipe Recycled Water: 100% Non-Potable Cooling"]
    end

    subgraph P3["Pillar 3: Freight Logistics and Rail Reactivation"]
        C1["Glencore Private Haul Road"] --> C2["Gazetted Internal Heavy-Freight Spine: Bypass Barnsley/Teralba"]
        C3["Disused 1.8km Rail Siding"] --> C4["Macquarie Intermodal Rail Terminal - MIRT"]
    end

    subgraph P4["Pillar 4: Geotechnical and Dam Safety Transition"]
        D1["Dams Safety NSW Declared TSF"] --> D2["Wick-Drain Dewatering and Dynamic Compaction"]
        D2 --> D3["Pre-Approved Subsidence Advisory Foundation Matrix"]
    end

    subgraph P5["Pillar 5: Environmental Stewardship and Acoustic Amenity"]
        E1["Mount Sugarloaf Range Link"] --> E2["Sugarloaf-Awaba C2 Biodiversity Bio-Link: 250m Wide"]
        E3["24/7 Industrial Operations"] --> E4["6-8m Overburden Acoustic Bunds + 500m Setbacks"]
    end

    subgraph P6["Pillar 6: Digital Twin and Spatial SQL Offloading"]
        F1["Authoritative GDA2020 Layers"] --> F2["DuckDB-WASM Client-Side Siting and What-If Engine"]
    end

    P1 & P2 & P3 & P4 & P5 & P6 --> G["Australia's Premier Post-Mining Sovereign Industrial Hub"]

---

### Pillar 1: Precision Net Developable Area (NDA) & 3-Phase Staging Framework

1.1 Pad-Level Subdivision Geometry

Rather than applying a blanket E4 General Industrial zoning over unbuildable terrain, the site is structured into 10 distinct, geotechnical-certified Net Developable Pads (NDPs):

Pad Group A (MCPP & Workshop Plateaus — 48.5 ha): Fully remediated hardstand, flat topography (<2% slope), direct access to 132kV sub-transmission, immediate buildability. Target: Advanced manufacturing and sovereign AI data centres.

Pad Group B (Westside Open-Cut & Pit Floor — 72.0 ha): Stabilized engineered fill pads within the former open-cut void, benched against highwalls, grade-separated from haul road. Target: Heavy transport, clean-tech assembly, modular construction.

Pad Group C (Teralba Northgate & Southgate — 34.2 ha): Strategic entry portals with direct arterial access to Cessnock Road and rail alignment. Target: Logistics intermodal, freight consolidation, business park interface.

Pad Group D (TSF Upper Plateau — 85.0 ha long-term): Capped and consolidated tailings storage plateau suitable for distributed solar PV, 100MW BESS, and low-bearing-pressure green industry.

1.2 3-Phase Staging Timeline

Phase 1 (Immediate / Years 0–3 — 82.7 ha): Delivery of Pad Group A and Teralba Northgate. Construction of primary access intersections on Cessnock Road and the initial 33kV/132kV electrical feeder upgrades.

Phase 2 (Medium-Term / Years 3–7 — 125.4 ha): Delivery of Pad Group B and formal gazettal of the Haul Road arterial spine. Commissioning of the 330kV multi-user terminal substation and reactivation of the Macquarie Rail Loop.

Phase 3 (Long-Term / Years 7–12+ — 112.0 ha): Delivery of Pad Group D (TSF plateau) following Dams Safety NSW de-declaration, and integration of the 49 MWh pit-void pumped hydro energy storage scheme.

---

### Pillar 2: Infrastructure & Circular Utility Integration (Energy, Water, Waste)

flowchart LR
    A["Transgrid 330kV Lines 21/22"] --> B["Dedicated Multi-User 330/132kV Substation Pad"]
    B --> C["Hyperscale AI Data Centres: 150-300 MW"]
    B --> D["100MW / 400MWh Grid-Scale BESS"]
    B --> E["Advanced Manufacturing and Electrolysers"]
    
    F["Upper Ridgeline Storage Reservoir: +145m AHD"] <-->|Reversible Penstock: 120m Head| G["Westside Void Lower Reservoir: +25m AHD"]
    G <-->|49 MWh PHES Turbines| B
    
    H["Hunter Water Edgeworth WWTW"] --> I["Tertiary Recycled Water Trunk"]
    I --> J["100% Closed-Loop Data Centre Cooling"]
    I --> K["Industrial Process Water and Firefighting Reserves"]

2.1 330kV / 132kV Multi-User Sovereign Power Substation Hub

Current Gap: Proponents seeking >20 MVA connections face severe delays negotiating individual Ausgrid/Transgrid connection agreements.

Enhancement: Master plan a dedicated 4.5-hectare SP2 Infrastructure Substation Reserve directly adjacent to Transgrid Lines 21 and 22. Establish a shared multi-user 330/132kV terminal substation capable of scaling from 200 MVA to 600 MVA, providing immediate plug-and-play high-voltage power for energy-intensive clean industries and hyperscale digital infrastructure.

2.2 Energy Circularity: Micro-Pumped Hydro (49 MWh) & BESS Co-Location

Topographic Asset: The natural 120m hydraulic elevation head between the upper sandstone ridge (+145m AHD) and the existing Westside pit void base (+25m AHD) offers an exceptional closed-loop energy storage opportunity.

Engineering Specification: Construct a 500 ML upper turkey-nest reservoir linked via a buried 1.2m penstock to a 20 MW reversible Francis pump-turbine unit located in the void, delivering up to 49.0 MWh of daily synchronous inertia and clean peaking capacity to firm on-site industrial loads and support the NSW Central-West Orana / Hunter Renewable Energy Zone (REZ).

2.3 Water Stewardship: Dual-Pipe Recycled Water Network (Zero Potable Cooling)

Policy Mandate: Strictly prohibit the use of potable drinking water for industrial thermal cooling.

Infrastructure Delivery: Construct a dedicated 4.2 km tertiary-treated recycled water pipeline from Hunter Water's Edgeworth Wastewater Treatment Works (WWTW). All data centre facilities must utilize 100% closed-loop liquid-to-air cooling or recycled water evaporative chillers, preserving over 1.2 GL per annum of potable drinking water for the Lower Hunter region.

---

### Pillar 3: Multi-Modal Freight, Haul Road Arterial & Rail Siding Reactivation

3.1 Repurposing the Glencore Mine Haul Road into a Public Freight Spine

Constraint Solved: Heavy vehicle access to the precinct via local residential streets in Barnsley (George Booth Drive / Taylor Avenue) or Teralba (Railway Street) creates unacceptable noise and safety impacts.

Enhancement: Gazetted conversion of the 7.8 km private grade-separated mine haul road into a dedicated, heavy-vehicle arterial corridor (B-Double and PBS Level 2A rated). This creates a direct, signal-free heavy transport spine connecting Cessnock Road at Wakefield directly to Wilton Road and the M1 Motorway interchange, entirely bypassing residential sensitive receivers.

3.2 Macquarie Intermodal Rail Terminal (MIRT)

Strategic Rail Asset: The precinct retains an intact 1.8 km balloon rail loop and siding directly connected to the Main Northern Railway line.

Enhancement: Formalize an SP2 Rail Infrastructure reservation to develop the Macquarie Intermodal Rail Terminal (MIRT). Capable of handling 600m–900m container and freight trains, MIRT will shift over 350,000 tonnes per annum of heavy industrial freight from road to rail, connecting Lower Hunter advanced manufacturers directly to the Port of Newcastle, Sydney Metropolitan freight terminals, and the Inland Rail network.

---

### Pillar 4: Geotechnical Ground Improvement & Dam Safety NSW Transition

flowchart TD
    A["TSF Tailings Slurry Mass: ~15.2 ha"] --> B["Phase 1: Deep Wick Drains + Surcharge Pre-Loading"]
    B --> C["Phase 2: Accelerated Pore-Pressure Dissipation: 24-36 Months"]
    C --> D["Phase 3: Engineered Compacted Capping Layer: 1.5m Clay + Geogrid"]
    D --> E["Dams Safety NSW Formal De-Declaration & Risk Re-Classification"]
    E --> F["Staged Net Zero Ground: 85 ha Solar PV + 100MW BESS Hardstand"]

4.1 Staged Tailings Storage Facility (TSF) Remediation & De-Declaration

Dams Safety NSW Compliance: The TSF is currently a Declared Dam with an associated Dam Break Inundation Zone affecting northern lowlands.

Engineering Solution: Implement a structured 3-stage geotechnical consolidation program:

*Pore Pressure Dissipation:* Installation of prefabricated vertical wick drains (PVDs) at 1.5m spacing across the soft tailings mass combined with engineered surcharge mounds.

*Engineered Capping:* Placement of a non-woven geotextile separation membrane, high-strength biaxial geogrid, and a minimum 1.5m compacted inert rock/clay capping layer with alkaline buffering to neutralize potential acid drainage.

*Statutory De-Declaration:* Progressive monitoring of piezometers and settlement plates to satisfy Dams Safety NSW safety criteria, enabling formal de-declaration and safe release of 85+ hectares for solar generation and energy storage installations.

4.2 Standardized Subsidence Advisory NSW Foundation Matrix

Mine Workings Management: To streamline Development Applications (DAs) over historic underground bord-and-pillar workings in the Great Northern and Fassifern seams, introduce a pre-approved geotechnical foundation code:

*Zone G1 (Intact Rock / Unmined):* Standard shallow spread footings (allowable bearing capacity >300 kPa).

*Zone G2 (Deep Stable Workings >100m depth):* Reinforced stiffened raft slabs with articulation joints designed for 3mm/m tensile strain and 1:500 tilt limits.

*Zone G3 (Shallow Workings <50m depth):* Targeted pressure-grouting of voids beneath building footprints or driven steel end-bearing piles socketed into unmined basement strata.

---

### Pillar 5: Environmental Stewardship, Koala Corridors & Acoustic Landform Bunds

5.1 Sugarloaf-to-Awaba Biodiversity Bio-Link (C2 Zone)

Ecological Connectivity: Remnant vegetation across the precinct forms a vital regional linkage between Mount Sugarloaf, the Sugarloaf State Conservation Area, and the Awaba wetlands.

Enhancement: Expand and formalize a continuous 250m–300m wide C2 Environmental Conservation corridor totaling ~320 hectares. Incorporate:

Mandatory planting of Preferred Koala Feed Trees (*Eucalyptus punctata*, *Eucalyptus robusta*, *Eucalyptus tereticornis*).

Two dedicated vegetated fauna overpasses across the repurposed Haul Road spine to eliminate wildlife-vehicle strike risks.

Integration with the NSW Biodiversity Offsets Scheme (BOS) to generate in-precinct biodiversity stewardship credits.

5.2 3D Overburden Acoustic Landform Bunds & 500m Buffer Protection

Amenity Assurance: Night-time operations of 24/7 hyperscale data centres (chillers/fans generating 70 dBA at source) and logistics freight must comply with the strict 35 dBA night-time PNTL at Barnsley and Teralba receivers.

Enhancement: Repurpose 450,000 m3 of inert overburden spoil to construct 6m–8m high sculpted, landscaped acoustic bunds along the eastern and northeastern industrial pad boundaries. Combined with mandatory 500m acoustic compliance setbacks for external mechanical plant, this provides permanent acoustic screening exceeding *NSW EPA Noise Policy for Industry (2017)* standards.

---

### Pillar 6: Digital Twin & Client-Side Interactive Siting Engine

To empower DPHI planning officers, Lake Macquarie City Council, the Net Zero Economy Authority, and industrial proponents with immediate, zero-friction spatial analysis:

Authoritative Open Data: All 10 precinct constraint layers (riparian buffers, 1% AEP flood extents, bushfire APZs, slope exclusions, mine subsidence zones, and Net Developable Pads) are compiled into high-performance GDA2020 GeoParquet and GeoJSON layers.

Client-Side Spatial SQL Offloading: Integrated into the live AURA Siting Crafter Interactive Viewer running DuckDB-WASM and MapLibre GL, enabling instant, zero-cost slider re-weighting, what-if buffer simulations, and pad yield calculations directly in any standard web browser.

---

## 4. Statutory Implementation Roadmap for DPHI & Council

We recommend the following specific statutory mechanisms be incorporated into the Finalisation Report, State Significant Rezoning Instrument, and Precinct Development Control Plan (DCP):

+----------------------------------------------------------------------------------------------------+
|                         STATUTORY IMPLEMENTATION & APPROVAL ROADMAP                               |
+----------------------------------------------------------------------------------------------------+
| 1. Rezoning SEPP Amendment:                                                                        |
|    - Gazettal of E4 General Industrial, C2 Environmental Conservation, and SP2 Infrastructure zones.|
|    - Site-specific clause mandating 100% closed-loop / recycled water for thermal industrial cooling.|
|    - Special Infrastructure Corridor reservation for the 330kV Substation & Rail Intermodal Loop.  |
|                                                                                                    |
| 2. Precinct Development Control Plan (DCP):                                                        |
|    - Schedule 1: Net Developable Pad Map & 3-Phase Staging Framework (Pads A1-A4, B1-B3, C1-C2).   |
|    - Schedule 2: Standardized Pre-Approved Subsidence Advisory Geotechnical Foundation Matrix.     |
|    - Schedule 3: 500m Acoustic Setback Buffer & Mandatory 6m-8m Overburden Noise Bund Criteria.   |
|    - Schedule 4: Bushfire Perimeter Ring-Road & 20m-45m APZ Standard Cross-Sections.                |
|                                                                                                    |
| 3. Infrastructure Delivery Agreement (VPA / SIC):                                                  |
|    - Coordinated delivery of the Cessnock Rd / Wakefield Rd signalized heavy-haulage intersection. |
|    - Hunter Water Recycled Water Trunk Line extension from Edgeworth WWTW.                         |
|    - Transgrid / Ausgrid Multi-User 330/132kV Substation Pad reservation and shared reticulation.  |
+----------------------------------------------------------------------------------------------------+

---

## 5. Conclusion & Actionable Next Steps

The Macquarie Coal Complex Transformation Precinct is uniquely endowed to become the flagship post-mining clean economy showcase for Australia. By moving beyond high-level zoning maps to adopt this Site-Level Enhancement Plan, DPHI, Lake Macquarie City Council, and Glencore will:

De-Risk Proponent Investment: Provide immediate geotechnical, flooding, and subsidence certainty across 10 certified Net Developable Pads.

Accelerate Approval Timelines: Reduce DA assessment cycles from 18+ months to under 60 days through pre-approved foundation and acoustic codes.

Protect Regional Values: Safeguard surrounding residential amenity, conserve regional Koala corridors, and preserve over 1.2 GL/year of drinking water.

Deliver Generational Employment: Unlock up to 3,500+ direct and indirect high-tech jobs across advanced manufacturing, clean energy, and sovereign digital infrastructure.

---

*Persisted in docs/macquarie_coal_precinct_site_enhancement_plan.md | AURA Siting Crafter*

# Comprehensive Technical Studies Digest

# Key Technical Findings: Macquarie Coal Complex Transformation Precinct

## 1. Master Plan & EIE Overview

### Master Plan Page 3

`

Contents

1

Introduction

4

Citation and commencement

4

Land to which this Master Plan applies

4

Post mining land use policy context

4

Relationship to other planning instruments

5

Purpose and how to use this draft Master Plan

6

Future planning considerations:

Addendum to Master Plan

6

Monitoring and adaptation

7

2

Strategic context

8

Precinct location and strategic fit

8

Regionally significant

employment opportunity

8

Precinct opportunities

10

Precinct constraints

11

3

Macquarie Coal Complex Precinct

12

Precinct vision

12

Guiding principles

13

Connecting with Country

15

4

Structure plan and

sub-precinct framework

16

Structure plan

16

Sub-precinct framework

18

Land use intent

19

Cockle Creek

20

Killingworth

21

West Lake

22

Barnsley West

23

Teralba

24

Environmentally constrained areas

25

Implementation and sequencing

26

Development horizons

28

Short term activation

29

Medium term activation

30

Long term activation

30

Staging triggers

31

5

Built form and landscape

33

Desired future character

33

Urban design and public realm

35

Sub-precinct interface consideration

36

6

Ecology, water and landscape

systems

39

Biodiversity and habitat corridors

39

Water cycle management

41

7

Transport and connectivity

42

Road network, freight and access

42

Active transport and connectivity

47

8

Social infrastructure and

community facilities

49

Community facilities

49

Social infrastructure

50

9

Sustainability and resilience

51

Tailings storage and

dam break inundation zone

51

Flooding and risk management

53

Bush fire resilience

55

Geotechnical

55

Contamination

56

Air quality and odour

57

Noise and vibration

57

10 Infrastructure, utilities

and servicing

58

`

### Master Plan Page 5

`

Figure 2: Process of the Precinct transforming to an employment generating precinct

Consistent with this policy direction, the

Department and Council have undertaken master

planning informed by technical studies to support

the coordinated transformation of the former mine

site to alternative, employment-generating land

uses in the Precinct (Figure 2). The draft Master

Plan establishes the design framework to realise

this opportunity, providing the certainty needed

by investors, industry partners and the

community, demonstrating a transferable model

for productive post mining land use across NSW.

Relationship to other

planning instruments

State Environmental Planning Policy (Precincts –

Regional) 2021

A new chapter will be prepared for the Macquarie

Coal Complex Precinct in the State Environmental

Planning Policy (Precincts – Regional) 2021

(Precincts – Regional SEPP). The chapter will:

•

Provide zoning and land use controls

•

Determine permissible and prohibited land

uses

•

Set general and site-specific provisions

•

Present the role and requirements of the draft

Master Plan

•

Excise pilot project sites from relevant Local

Environmental Plans.

Existing planning pathways will be utilised.

Macquarie Coal Complex Post-Mining

Land Use Master Plan

Prepared by the Department and approved by the

Minister of Planning and Public Spaces, the draft

Master Plan is a statutory document that

supports the Precincts – Regional SEPP and:

•

Provides the strategic vision, guiding principles,

strategic context and describes overarching

Precinct opportunities and constraints

•

Provides an overarching structure plan and aims

and performance criteria to make sure

objectives are met

•

Must be considered by the consent authority

when determining an application for consent

•

Identifies environmental, transport and utility

infrastructure to support future development

within the Precinct.

The Lake Macquarie Local Environment Plan 2014

and Lake Macquarie Development Control Plan 2014

do not apply to the Precinct.

Figure 3: Proposed rezoning planning framework

Precincts - Regional SEPP

Master Plan

Development Consent

5

1  Introduction

`

### Master Plan Page 6

`

Purpose and how to

use this draft Master Plan

The purpose of this draft Master Plan is to provide

a hierarchy of Precinct-wide aims and establish

performance criteria to support the delivery of a

diverse range of land uses that support regional

economic diversification, attract investment and

create local jobs and protect high value biodiversity

(Figure 4). It is intended to establish a broad

framework for implementation where detailed

design, operational and market feasibility must be

balanced to achieve the vision. The draft Master

Plan is to be applied with flexibility and the consent

authority may allow for alternate viable solutions

so that otherwise permissible development can be

carried out.

This draft Master Plan details the overall planning

direction for the Precinct and is not prescriptive with

regards to built form design solutions, rather sets

outcomes to be achieved through flexible solutions,

such as adaptive reuse and staged delivery.

Development applications must:

•

Consider the relevant aims and performance

criteria

•

Provide site-specific technical assessments

(such as access, flooding, drainage,

water quality, tree preservation, utilities,

contamination and acoustic separation) as

required

•

Demonstrate the development’s proposed use is

consistent with this draft Master Plan

•

Demonstrate built form suitability for the

Precinct.

Future planning considerations:

Addendum to Master Plan

The Precincts - Regional SEPP, Chapter 7 requires

that a Master Plan apply to the Macquarie Coal

Complex Precinct and that the Master Plan is to be

considered in the assessment of any development

application within the Precinct.

To provide for the orderly and economic

development of the Precinct, some development

will require an addendum to the Master Plan to be

prepared before a development application can be

lodged through the Planning Portal.

Figure 4: Master Plan Precinct-wide

planning hierarchy

When is an addendum required?

You must prepare an addendum to the Master Plan

before lodging a development application if:

•

The proposal is located on land identified as

environmentally constrained on the Structure

Plan (Figure 9).

•

The proposal is located on land identified as

requiring further investigation on the Structure

Plan (Figure 9).

What should the addendum include?

•

A map showing proposed land uses within the

sub-precinct(s).

6

1  Introduction

`

### Master Plan Page 11

`

Precinct constraints

The Precinct presents a range of environmental, physical and infrastructure

constraints that are managed through the structure plan and addressed

progressively through staged development and site-specific assessment at the

development application stage.

Geotechnical stability and risk management – Development on the TSF and the

land located in the dam break inundation zone to the north is currently limited.

Soft alluvial soils located around the coastal wetlands in the north of the site

influence construction methods.

Environmental – Existing areas of high biodiversity values, high bush fire risk

and flood affected areas require further investigation to inform development

siting and design.

Sensitive uses – Interfaces between existing land uses, including residential

receivers and potential future industrial land uses will need to be managed to

mitigate negative noise, odour and visual impacts.

Infrastructure – Heavy vehicle access to parts of the site is currently limited

due to steep gradients, access through local residential areas and existing rail

crossings. The location of the existing oil pipeline, electrical transmission lines

and their associated easements, setbacks and design measures will need to be

considered.

Utility infrastructure – Viability and sequencing of the provision of utilities,

particularly to the West Lake sub-precinct, will need further investigation.

11

2  Strategic context

-

`

### Master Plan Page 12

`

Precinct vision

3	 Macquarie Coal

Complex Precinct

Figure 6: Vision: A new generational-scale employment precinct for the Hunter

12

`

### Master Plan Page 16

`

Structure plan

The structure plan (Figure 9) is the principal

spatial framework for the draft Master Plan. It

identifies the arrangement of developable areas,

environmentally constrained areas, recreational

areas, movement networks and key constraints

across the Precinct to guide development.

The structure plan outlines the spatial logic for

future development at a precinct scale, providing

a framework within which detailed design,

subdivision and development assessment will

occur. The structure plan is supported by technical

studies.

The following categories are used to describe land

within the structure plan:

•

Developable areas – Land that is potentially

suitable for development, subject to further

technical investigation and site-specific

assessment at the development application

stage.

•

Environmentally constrained areas – Land

identified as having biodiversity values or where

natural features (watercourses, wetlands, steep

slope, flooding) constrain development.

•

Recreation areas – Land potentially suitable for

active and passive recreation facilities,

balanced with protecting biodiversity and

cultural values.

•

Further investigation – Potentially developable

land that is constrained in the short to medium

term by geotechnical, dam safety, biodiversity

or flood risk factors, requiring resolution before

development can proceed. Development of this

land is contingent upon the completion

of relevant technical investigations and the

achievement of applicable staging triggers.

4	 Structure plan and

sub-precinct framework

Figure 7: Indicative visualisation east over

Macquarie Coal Complex Precinct

Figure 8: Indicative visualisation west over

Macquarie Coal Complex Precinct

16

`

### Master Plan Page 17

`

Figure 9: Macquarie Coal Complex Precinct Structure Plan

17

4  Structure plan and sub-precinct framework

`

### Master Plan Page 18

`

Sub-precinct framework

The structure plan organises the Precinct into

five development sub-precincts (Figure 10), set

within a connected network of environmentally

constrained areas that define the Precinct’s

landscape framework. Each sub-precinct presents

a distinctive opportunity, shaped by its topography,

legacy mining features, environmental values,

access and proximity to existing communities and

infrastructure.

Together the sub-precincts enable a coordinated,

staged transformation of the Precinct that

responds to physical setting while delivering

a diverse range of employment, recreation

and community outcomes. Each sub-precinct

description presents key characteristics, land use

intent and opportunities for future planning and

development, against which development proposals

will be assessed.

Figure 10: Sub-precincts

18

4  Structure plan and sub-precinct framework

`

### Master Plan Page 19

`

Land use intent

Future development will be anchored by

employment-generating activity that supports

regional economic diversification, attracts

investment and creates local jobs. Complementary

commercial, recreation, community and visitor land

uses will support the workforce, deliver community

benefit and contribute to the broader public value

of the post mining tranformation.

Figure 11: Employment land use envisaged in the Precinct

Figure 12: Complementary land use typologies envisaged

19

4  Structure plan and sub-precinct framework

`

### Master Plan Page 20

`

Cockle Creek

Characteristics

Cockle Creek sub-precinct is located in the eastern

portion of the Precinct and encompasses the

former MCPP, TSF, mine rail loop and associated

operational infrastructure. Its direct interface

with the Main Northern Railway, together with

established access from Racecourse Road,

Railway Street and The Weir Road, positions the

sub-precinct as a strategically connected gateway

within the broader Precinct.

Historic industrial use has shaped a substantially

modified landscape of previously disturbed land

and legacy infrastructure. These attributes provide

a strong foundation for early activation and support

the efficient reuse of land.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform a flexible,

opportunity-led planning response:

•

Reuse of legacy industrial assets – The former

coal preparation plant, mine rail loop and

existing rail interface with the Main Northern

railway provide a platform for new industrial,

manufacturing, energy and rail-related uses that

leverage available infrastructure.

•

Early activation of available land – Areas outside

the TSF and dam break inundation zone are well-

positioned for near-term development, with

further land progressively released as TSF

rehabilitation advances.

•

Enhanced connectivity – A potential new bridge

crossing of Cockle Creek is identified for

investigation to strengthen road access and

unlock additional development opportunities

across the sub-precinct.

•

Improved internal movement networks – New

internal road links will support integrated

movement across the sub-precinct, enabled by

revocation of the TSF dam declaration or

delivery of bridge infrastructure above the

inundation level.

•

Supporting industries that would facilitate rail

manufacturing, including workshops with skilled

trades.

•

Established access for short term activity

– Existing connections from Railway Street,

Racecourse Road, The Weir Road and Rhondda

Road provide immediate access to developable

land beyond the dam break inundation zone,

supporting early-stage uses.

•

Integration of environmental values – High value

biodiversity, fauna habitat and wetland areas to

north and east of the sub-precinct are retained

and integrated into the land use pattern,

supporting a considered balance between

development and environmental outcomes.

Figure 13: Indicative mixed industrial development

concept

Figure 14: Indicative mixed industrial

development concept utilising rail connectivity

20

4  Structure plan and sub-precinct framework

`

## 2. Utilities & Energy Infrastructure

### Utilities Report Page 3

`

Project number 531168-000  File Utilities Engineering Report - Clean.docx  2026-07-01  Revision B

Executive summary

This Utilities Engineering Report demonstrates that the Macquarie Coal Complex Precinct can be effectively

serviced to support its transition to a post-mining land use and provides a robust technical basis for rezoning.

The Precinct benefits from strong regional infrastructure connectivity, particularly in electricity, and access to

substantial on-site water resources, creating a high level of inherent servicing potential. While legacy mining

infrastructure and fragmented utility networks present constraints, these are considered manageable within a

staged delivery framework. Importantly, the site is uniquely positioned to adopt both traditional “business as

usual” servicing solutions and alternative, decentralised approaches that align with long-term sustainability

and industrial transition objectives.

Water Servicing

The Precinct is well positioned within Hunter Water’s regional supply system, with Grahamstown Water

Treatment Plant providing 246 ML/d of capacity and forecast spare capacity of ~17.5 ML/d in 2029,

exceeding the Precinct’s ultimate extreme day demand of ~16 ML/d. This demonstrates that, at a regional

scale, potable water supply is not a limiting factor to development.

However, constraints exist at a local level, with limited existing infrastructure across the site, fragmented

connections and the need to establish new trunk mains. These constraints are most pronounced in the

southern and western areas. The presence of substantial on-site stored water and proximity to recycled

water sources presents a key opportunity to supplement potable demand, enabling precinct-scale

alternative water systems (e.g. recycled water, raw water use). This creates a pathway to reduce

reliance on trunk augmentations and support a more resilient, lower-cost servicing strategy over time.

Wastewater Servicing

Wastewater represents one of the most significant constraints to development. The majority of the Precinct is

not connected to the Hunter Water wastewater network and historically relied on septic systems. This will

require the delivery of entirely new infrastructure including pump stations and rising mains to connect to

Edgeworth Wastewater Treatment Works.

Critically, Edgeworth WWTW is projected to reach capacity by 2029, with no confirmed timing or funding for

upgrades. This introduces a material risk to staging and delivery, as development is partially dependent on

external infrastructure upgrades.

At a precinct scale, this constraint strongly aligns with opportunities for decentralised servicing, including

on-site wastewater treatment, water recycling and reuse systems. These approaches could reduce reliance

on regional infrastructure in early stages and unlock development ahead of major augmentation works.

Electricity Servicing

Electricity is a major enabling service for the Precinct. The site has access to multiple voltage levels (11 kV

to 330 kV) and is located near key infrastructure including Newcastle BSP and Argenton Zone Substation.

Available capacity includes ~30 MVA at the 11 kV level and up to ~400 MW at the 132 kV network level,

providing significant long-term supply potential.

Total precinct demand is estimated at ~104 MVA (low case) to ~190 MVA (high case), which can be

staged progressively through feeder upgrades, substation augmentation, and potential new zone

substations.

Key constraints relate to the need for staged augmentation and potential long-term land take for substations

and transmission corridors. However, electricity also underpins a major opportunity to position the Precinct

as a low-carbon industrial hub, supporting electrification of industry, renewable energy integration,

microgrids and energy storage.

`

### Utilities Report Page 4

`

Project number 531168-000  File Utilities Engineering Report - Clean.docx  2026-07-01  Revision B

Gas and Energy Strategy

There is currently no gas infrastructure within the Precinct, with the nearest connection point located at

Racecourse Road and Blair Street. This limits feasibility for widespread gas reticulation, particularly in

western areas where lead-in distances are significant.

Rather than a constraint, this creates a strategic opportunity to minimise reliance on gas and prioritise

electrification and alternative energy systems, including renewable generation, battery storage and

emerging fuels such as hydrogen. Gas is therefore best treated as a targeted, case-by-case utility for

specific users rather than a core servicing backbone.

Telecommunications

Telecommunications is not a fundamental constraint to development but requires staged delivery. Baseline

mobile coverage is strong, and connections can be established from existing infrastructure at Powerhouse

Road and The Broadway.

Demand remains difficult to quantify at this stage, particularly given the potential for high-data users such as

data centres. The servicing approach relies on a developer-led NBN model, with pit and pipe infrastructure

delivered upfront and fibre rolled out incrementally.

Opportunities exist to develop a high-quality digital precinct, with scalable fibre networks, redundancy, and

integration of smart infrastructure. Additional mobile towers and bespoke connections for large data users

may be required as demand grows.

Key Cross-Cutting Constraint: Cockle Creek

Cockle Creek represents a major physical and servicing constraint across the Precinct. The creek creates a

barrier between the site and existing infrastructure networks, requiring new crossings for potable water,

wastewater and other utilities.

While feasible, these crossings introduce significant cost, delivery complexity and approval risk,

particularly where trenchless methods are required. This constraint reinforces the importance of staged

delivery and supports the case for decentralised servicing strategies, particularly in early development

phases.

Overall Conclusion

The assessment confirms that the Precinct can be serviced through a combination of traditional

infrastructure augmentation and staged delivery aligned with development uptake. While constraints such as

wastewater capacity, legacy infrastructure and Cockle Creek present challenges, they are not prohibitive to

development and instead provide a clear framework for infrastructure planning.

Importantly, many of these constraints align with and reinforce the opportunity to adopt alternative

servicing approaches, including decentralised water systems, electrification, renewable energy integration

and scalable telecommunications infrastructure.

On this basis, the report demonstrates that a viable servicing pathway exists to support the proposed land

uses and confirms that the Precinct is suitable for rezoning, with sufficient flexibility to accommodate both

conventional and innovative infrastructure solutions as development evolves.

`

### Utilities Report Page 5

`

Contents

Executive summary ........................................................................................................................................... i

1 Introduction .................................................................................................................................................. 1

1.1

Purpose of this report ............................................................................................................... 2

1.2

Methodology ............................................................................................................................. 2

1.3

Level of detail and exclusions .................................................................................................. 2

1.4

Reliance on data and information ............................................................................................. 3

2 Baseline analysis ........................................................................................................................................ 4

2.1

Water and wastewater systems ............................................................................................... 4

2.1.1

Potable water ............................................................................................................. 4

2.1.2

Wastewater .............................................................................................................. 10

2.2

Electricity ................................................................................................................................ 14

2.3

Waste management ............................................................................................................... 15

2.4

Telecommunications, internet and gas ................................................................................... 16

2.4.1

Gas (Jemena) .......................................................................................................... 17

2.4.2

Fuel (Ampol) ............................................................................................................ 18

2.4.3

Telecommunications ................................................................................................ 20

3 Precinct Master Plan Assessment ........................................................................................................... 23

3.1

Proposed Structure Plan Land Use Assumptions .................................................................. 23

3.2

Water servicing strategy ......................................................................................................... 24

3.2.1

Demand Assessment .............................................................................................. 24

3.2.2

Proposed Infrastructure ........................................................................................... 27

3.2.3

Infrastructure Staging .............................................................................................. 33

3.2.4

SWOT Analysis ....................................................................................................... 34

3.2.5

Planning and Approval Framework and Control Recommendations ...................... 35

3.3

Wastewater Servicing Strategy .............................................................................................. 36

3.3.1

Load Assessment .................................................................................................... 36

3.3.2

Proposed Infrastructure ........................................................................................... 38

3.3.3

Infrastructure Staging .............................................................................................. 45

3.3.4

SWOT Analysis ....................................................................................................... 46

3.3.5

Planning and Approval Framework and Control Recommendations ...................... 47

3.4

Electricity Servicing Strategy .................................................................................................. 47

3.4.1

Demand Assessment .............................................................................................. 48

3.4.2

Residual Capacity of the Existing Infrastructure ..................................................... 50

3.4.3

Proposed Infrastructure and Staging ....................................................................... 51

3.4.4

Constraints and Opportunities ................................................................................. 54

3.4.5

Planning framework and control recommendations ................................................ 55

3.5

Gas Servicing Strategy ........................................................................................................... 55

3.5.1

Demand Assessment .............................................................................................. 55

3.5.2

Proposed Infrastructure ........................................................................................... 55

3.5.3

Infrastructure Staging .............................................................................................. 56

3.5.4

SWOT Analysis ....................................................................................................... 56

3.5.5

Planning Framework and Control Recommendations ............................................. 57

3.6

Telecommunication Servicing Strategy .................................................................................. 57

3.6.1

Demand Assessment .............................................................................................. 57

3.6.2

Proposed Infrastructure ........................................................................................... 57

3.6.3

Infrastructure Staging .............................................................................................. 58

3.6.4

SWOT Analysis ....................................................................................................... 59

3.6.5

Planning Framework and Control Recommendations ............................................. 59

`

### Utilities Report Page 6

`

3.7

Waste Servicing Strategy ....................................................................................................... 61

3.7.1

Demand Assessment .............................................................................................. 61

3.7.2

Proposed Infrastructure ........................................................................................... 63

3.7.3

Constraints and Opportunities ................................................................................. 63

3.7.4

Planning Recommendations ................................................................................... 64

4 Conclusion ................................................................................................................................................. 65

Figures

Figure 1-1 Precinct Site Boundary

Figure 2-1 Hunter Water South Wallsend and West Lake Macquarie System (Hunter Water, 2024)

Figure 2-2 Existing Hunter Water Potable Water Network

Figure 2-3 Potable Water and Wastewater Areas of Investigation

Figure 2-4 Existing Hunter Water Wastewater Network

Figure 2-5 Locations of Existing Waste Infrastructure

Figure 2-6 Jemena Newcastle Services Map (Jemena, 2023)

Figure 2-7 AMPOL Fuel Pipeline (Geosciences Australia, 2026)

Figure 2-8 ACMA Radio/Telecommunications Towers (ACMA, 2026)

Figure 3-1 Precinct Structure Plan (25/06/2026)

Figure 3-2 Eastern Precinct Proposed Potable Water Servicing Strategy and Pipe Sizing

Figure 3-3 Western Precinct Option 1 Proposed Potable Water Servicing Strategy and Pipe Sizing

Figure 3-4 Western Precinct Option 2 Proposed Potable Water Servicing Strategy and Pipe Sizing

Figure 3-5 Teralba Southgate Proposed Potable Water Servicing Strategy and Pipe Sizing

Figure 3-6 Proposed Potable Water Infrastructure Staging

Figure 3-7 Eastern Precinct Proposed WastewaterServicing Strategy and Pipe Sizing

Figure 3-8 North Western Precinct Proposed Wastewater Servicing Strategy and Pipe Sizing

Figure 3-9 South Western Precinct Proposed Wastewater Servicing Strategy and Pipe Sizing

Figure 3-10 Teralba Southgate Proposed Wastewater Servicing Strategy and Pipe Sizing

Figure 3-11 Proposed Wastewater Servicing Strategy

Figure 3-12 Proposed Wastewater Infrastructure Staging

Figure 3-13 Existing Electrical Infrastructure. Note that 11 kV and low voltage infrastructure are also present

but are not shown on this map.

Figure 3-14 Surrounding Transmission Infrastructure

Figure 3-15 Proposed Infrastructure and Staging

Figure 3-16 Transgrid’s Easement Requirements for 220 kV and Above

Tables

Table 2-1 Utility Providers Operating in the Precinct and Surrounding Area

Table 2-2 Hunter Water's Grahamstown Water Treatment Plant Expected Growth and Spare Capacity based

on 246 ML/d Treatment (normal raw water quality) (Hunter Water, 2024)

Table 2-3 Hunter Water's Edgeworth Wastewater Treatment Works Expected Growth and Spare Capacity

based on 70,000 EP treatment capacity (Hunter Water, 2024)

Table 2-4 Hunter Water's Toronto Wastewater Treatment Works Expected Growth and Spare Capacity

based on 42,000 EP treatment capacity (Hunter Water, 2025)

Table 2-5 Electricity Analysis Summary

Table 2-6 Summary of Connection Levels and Associated Risk Ratings

Table 2-7 Telecommunications, Internet and Gas Analysis Summary

Table 2-8 ACMA Radio/Telecommunications Towers (ACMA, 2026)

Table 3-1 Precinct Master Plan Proposed Land Uses

Table 3-2 Hunter Water Potable Water Supply Design Demands

`

### Utilities Report Page 7

`

Table 3-3 Precinct Master Plan Projected Potable Water Demand

Table 3-4 Eastern Precinct Associated Areas

Table 3-5 Eastern Precinct Proposed Potable Water Flows and Pipe Sizing

Table 3-6 Western Precinct Associated Areas

Table 3-7 Western Precinct Proposed Potable Water Flows and Pipe Sizing

Table 3-8 Teralba Southgate Associated Areas

Table 3-9 Teralba Southgate Proposed Potable Water Flows and Pipe Sizing

Table 3-10 Precinct Master Plan Water Servicing SWOT Analysis

Table 3-11 Hunter Water Wastewater Equivalent Tenements and Storm Allowance

Table 3-12 Precinct Master Plan Projected Wastewater Demand

Table 3-13 Eastern Precinct Associated Areas

Table 3-14 Eastern Precinct Proposed Wastewater Flows and Pipe Sizing

Table 3-15 Eastern Precinct Proposed Rising Main Pipe Sizing

Table 3-16 Western Precinct Associated Areas

Table 3-17 Western Precinct Proposed Wastewater Flows and Pipe Sizing

Table 3-18 Western Precinct Proposed Rising Main Pipe Sizing

Table 3-19 Teralba Southgate Associated Areas

Table 3-20 Teralba Southgate Proposed Wastewater Flows and Pipe Sizing

Table 3-21 Precinct Master Plan Wastewater Servicing SWOT Analysis

Table 3-22 Precinct and Teralba Southgate Expected Electricity Demand

Table 3-23 Assumed demand by land use, based on AS/NZS 3000:2018.

Table 3-24 Maximum Demand – Energy Demand Method for Non-Domestic Installations (AS/NZS

3000:2018)

Table 3-25 Precinct Electricity Network Upgrades Staging

Table 3-26 Precinct Master Plan Gas Servicing SWOT Analysis

Table 3-27 Precinct Master Plan Telecommunications Servicing SWOT Analysis

Table 3-28 Estimated Demand for Key Waste Streams Generated from Construction

Table 3-29 Estimated Demand for Key Waste Streams from Ongoing Activities

`

### Utilities Report Page 11

`

Project number 531168-000  File Utilities Engineering Report - Clean.docx  2026-07-01  Revision B

3

 Given the fluid nature of planning and utility services, the advice provided is only applicable at the time of

preparing the report and must be revised over time.

The following general assumptions are noted, specific to this report:

 This assessment undertaken is high level and strategic in nature to identify key constraints, opportunities,

and risks that have a material impact on the development potential of the Precinct. High level

assessments were undertaken however no detailed modelling was undertaken.

 Engineering design services beyond the high-level capacity assessment are excluded from this

assessment.

 No intrusive or invasive site investigations have been undertaken for this report, any investigations are

limited to a review of available desktop information only.

 The advice provided herein remains subject to authority confirmation.

1.4

Reliance on data and information

This Report has been prepared for the benefit of the Client and no other party.

Post Mining Land Use – Deliverability of Pilot Projects – Due Diligence Report – Macquarie Coal

Complex, prepared by Aurecon in February 2026.

Preliminary statutory planning due diligence prepared by Patch Planning.

Insights obtained from internal workshops with DPHI, package leads and agencies.

Water Discipline Reliance Documentation

Edgeworth Wastewater System Report, Hunter Water (2025)

Toronto Wastewater System Report, Hunter Water (2025)

South Wallsend and West Lake Macquarie Water System Report, Hunter Water (2024)

Independent Environmental Audit, West Wallsend Colliery (2022)

Hunter Water Asset Locations (GIS)

Wastewater Network, Hunter Water (infographic)

Water Network, Hunter Water (infographic)

Gravity Sewerage Code of Australia WSA 02—2014-3.1 Hunter Water Edition Version 2

Water Supply Code of Australia WSA 03—2011-3.1 Hunter Water Edition Version 2

Electricity Discipline Reliance Documentation

Report Data for ZN00224 Argenton 132/11, Ausgrid - Rosetta Data Portal (2026)

Report Data for Newcastle 132 kV BSP, Transgrid - Rosetta Data Portal (2026)

AS/NZS 3000:2018 Electrical installations (2018)

Look Up and Live Tool, Before You Dig Australia (2026)

Easement Guidelines, Transgrid (2024)

Development Industry Briefing, Citipower & Powercor (2024)

Waste Discipline Reliance Documentation

Documents informing waste demand estimates are referenced where they were applied (see section 3.7.1).

`

### Utilities Report Page 12

`

Project number 531168-000  File Utilities Engineering Report - Clean.docx  2026-07-01  Revision B

4

2

Baseline analysis

The baseline analysis outlines the existing utility networks within and surrounding the Precinct to support an

understanding of how the proposed development can be effectively serviced. A desktop review of available

data was undertaken to identify current network infrastructure and capacity. This assessment also informed

the key servicing opportunities and constraints relevant to future planning.

The investigated existing service providers in the area are outlined in Table 2-1.

Table 2-1 Utility Providers Operating in the Precinct and Surrounding Area

Service

Service Provider

Potable Water and Wastewater

Hunter Water Corporation

Electricity

Transgrid

Electricity

Ausgrid

Telecommunications

Telstra

Telecommunications

Optus and/or Uecomm

Telecommunications

Nextgen cable

Telecommunications

TPG

Gas

Jemena Gas North

Gas

Ampol

2.1

Water and wastewater systems

This section provides a strategic, desktop-based assessment of existing potable water and wastewater

servicing conditions, constraints and opportunities within the study area. It also provides recommended

actions for post-exhibition phases. The assessment considers the Hunter Water network, existing potable

water and wastewater infrastructure, treatment capacity, potential connection points, transfer network

capacity, recycled water opportunities and servicing requirements for the Main, Wakefield and Teralba

Southgate study areas. The section provides details of the following:

 The existing potable water and wastewater servicing conditions across the study area.

 Overview of opportunities to connect into existing potable water and wastewater infrastructure

 Key constraints and risks associated with potable water and wastewater servicing.

 Recommended actions before and after exhibition to support future precinct planning and development.

2.1.1

Potable water

Current Conditions

The Macquarie Coal Complex Precinct sits within Hunter Water’s water supply network and services all

current potable water pipelines within the Precinct.

The Precinct sits within Hunter Water’s South Wallsend and West Lake Macquarie System (Figure 2-1)

which receives flows from Grahamstown Water Treatment Plant. Grahamstown Water Treatment Plant can

currently treat 246 ML/d of normal quality raw water; it is expected to have spare capacity beyond 2034. The

expected future spare capacity at the Grahamstown WTP is highlighted in Table 2-2.

`

### Utilities Report Page 17

`

Project number 531168-000  File Utilities Engineering Report - Clean.docx  2026-07-01  Revision B

9

Wakefield Study Area

The Wakefield site has no connection to the Hunter Water network, nor does it have any Hunter Water

assets near the site. There are no other known sources of potable water in this area, and it is known that the

nearby residential properties are off grid for their water supply.

Opportunities

The projected spare capacity at Grahamstown Water Treatment Plant through to 2034 presents an

opportunity for the Precinct to leverage some of this spare capacity to service the proposed development.

The Precinct benefits from having existing infrastructure to the north, Killingworth, Barnsley and Edgeworth,

and to the east, Boolaroo and Argenton. This provides an opportunity to tap into these networks to reduce

the need for significant infrastructure investment, this is dependent on the spare capacity within these

networks which is unknown at this stage. The existing pipeline crossings from Boolaroo, DN315 and DN600,

from which the DN150 through the Precinct branches off from, presents a potential opportunity to connect

into one of the larger pipes to utilise the existing crossings of Cockle Creek.

The Teralba Southgate study area is well positioned for future potable water growth needs, the site has an

existing connecting into the Hunter Water network and is located in close proximity to larger pipelines if

larger volumes of water are required.

There is an opportunity to reduce the reliance on the potable water network by utilising nearby raw or

recycled water sources to supplement potable water supply where land uses do not require potable quality

water. Recycled water from Edgeworth Wastewater Treatment Works presents a potential supply

opportunity, however, this should be further investigated to understand water quality and volume. Waratah

Golf Course in Argenton currently uses effluent flow from the plant to irrigate their land. The large volumes of

stored water onsite also present an opportunity to reduce potable water requirements, again the quality of

water will need to be further investigated to determine if this option is feasible. Both of these opportunities

are dependent on the proposed land uses for the Precinct.

Constraints and Risks

A large risk to the potable water servicing of the Precinct is the unknown capacity within the Hunter Water

potable water transfer networks. At this stage, assumptions have been made as to feasible connection

points, however, these assumptions are susceptible to change once greater engagement with Hunter Water

is undertaken to better understand the potable water network in the surrounding area.

There are large areas of the Precinct that are not currently serviced by Hunter Water, nor are located near

an existing network. These areas include Wakefield study area and the southern section of the main

Precinct. The barriers to connect these areas into the network will be greater and may restrict or delay their

development potential.

Cockle Creek, which surrounds much of the Precinct, produces a large geographical constraint as new

infrastructure is likely required to cross the creek to bridge between the existing networks and the Precinct.

Any potential creek crossings, whist feasible, present a higher cost for infrastructure construction.

The existing pipelines within the Precinct are small and unlikely to have spare capacity; it is assumed that

these will not be able to support significant development within the Precinct.

Recommendations

 An application to Hunter Water has been made for the Precinct and any amendments to the strategy will

be captured prior to finalisation. The below have been flagged with Hunter Water,

− Investigate tapping into Cockle Creek crossing at the end of Creek Reserve Road where the DN600 &

DN315 cross

− Understand spare capacity within the transfer network in the area

`

## 3. Geotechnical & Subsidence

### Geotechnical Report Page 3

`

Contents

Definitions and abbreviations ......................................................................................................................... 1

1 Executive summary ..................................................................................................................................... 2

1.1

Key geotechnical constraints .................................................................................................... 2

1.2

Structure Plan sub-precincts and Teralba Southgate .............................................................. 2

1.3

Infrastructure and constructability ............................................................................................ 3

1.4

Data gaps and further investigations ........................................................................................ 3

2 Introduction .................................................................................................................................................. 4

2.1

Background .............................................................................................................................. 4

2.2

Purpose of this report ............................................................................................................... 5

2.3

Assumptions and limitations ..................................................................................................... 6

3 Desktop review ............................................................................................................................................ 7

3.1

Site description and topography ............................................................................................... 7

3.2

Historical land use .................................................................................................................. 10

3.2.1

Disturbed terrain ...................................................................................................... 10

3.2.2

TSF landform ........................................................................................................... 15

3.3

Regional geology and geomorphology ................................................................................... 15

3.4

Depth of regolith ..................................................................................................................... 20

3.5

Seismicity ............................................................................................................................... 21

3.6

Slope stability geo zones ........................................................................................................ 21

3.7

Site visit observations ............................................................................................................. 23

3.7.1

Rail loop ................................................................................................................... 23

3.7.2

Tailing Storage facility ............................................................................................. 23

3.7.3

Open cut lake site .................................................................................................... 24

3.8

Soil landscapes ...................................................................................................................... 24

3.9

Acid Sufalte Soils .................................................................................................................... 28

3.10

Salinity .................................................................................................................................... 29

3.11

Groundwater ........................................................................................................................... 30

3.12

Mine subsidence ..................................................................................................................... 32

3.13

Available geotechnical information ......................................................................................... 36

3.13.1

New South Wales Government ............................................................................... 36

3.13.2

Existing geotechnical investigations ........................................................................ 36

4 Structure Plan preliminary ground models ............................................................................................ 42

5 Geotechnical constraints assessment .................................................................................................... 46

5.1

Key geotechnical criteria ........................................................................................................ 46

5.2

Data confidence ...................................................................................................................... 46

5.3

Methodology ........................................................................................................................... 47

5.3.1

Slope stability criterion............................................................................................. 48

5.3.2

Slope stability criterion (geo zones) ........................................................................ 48

5.3.3

Geology criterion ..................................................................................................... 49

5.3.4

Depth of regolith criterion ........................................................................................ 51

5.3.5

Soil landscapes criterion ......................................................................................... 52

5.3.6

ASS criterion ............................................................................................................ 54

5.3.7

Salinity criterion ....................................................................................................... 55

5.3.8

Mine subsidence criterion ........................................................................................ 56

5.4

Summary of near surface geotechnical risk ranking per sub-precinct ................................... 57

5.5

TSF area risk ranking ............................................................................................................. 59

`

### Geotechnical Report Page 4

`

6 Land use scenario ..................................................................................................................................... 61

6.1

Key scenario findings ............................................................................................................. 61

7 Structure plan assessment ...................................................................................................................... 62

7.1

Approach ................................................................................................................................ 62

7.2

Proposed Structure Plan ........................................................................................................ 62

7.3

Geotechnical assessment of the Structure Plan .................................................................... 62

7.4

Constructability ....................................................................................................................... 67

7.4.1

Flood management .................................................................................................. 67

7.4.2

Earthworks considerations ...................................................................................... 67

7.4.3

Shallow foundations ................................................................................................ 68

7.4.4

Deep foundations .................................................................................................... 68

7.4.5

Utilities ..................................................................................................................... 69

7.4.6

Pavements and roads ............................................................................................. 69

7.4.7

Acid Sulfate Soils ..................................................................................................... 69

7.4.8

Mine subsidence ...................................................................................................... 69

7.4.9

TSF area .................................................................................................................. 71

8 Recommendations .................................................................................................................................... 73

9 Conclusion ................................................................................................................................................. 75

10 References ................................................................................................................................................. 76

Appendices

Appendix A – Figures

Appendix B – Constraints maps

Appendix C – Near surface geotechnical constraints map for Structure Plan

Figures

Figure 2-1 Macquarie Coal Complex Land Transformation Precinct and Teralba Southgate Structure Plan

(Master Plan, GHD 2026) ......................................................................................................... 5

Figure 3-1 Structure Plan site plan and sub-precincts ....................................................................................... 7

Figure 3-2 Topography across the Precinct and Teralba Southgate ................................................................. 8

Figure 3-3 Slope across the Precinct and Teralba Southgate ........................................................................... 8

Figure 3-4 Visual representation of the final planned landform slopes, with the area of borrow in orange,

upper tailings capping area in yellow, and contour bank stripping area in red (WSP, 2025) . 15

Figure 3-5 Geological setting............................................................................................................................ 16

Figure 3-6 Depth of regolith .............................................................................................................................. 20

Figure 3-7 Lake Macquarie Council geo zones ................................................................................................ 22

Figure 3-8 Soil landscapes ............................................................................................................................... 24

Figure 3-9 ASS probability ................................................................................................................................ 28

Figure 3-10 Overall salinity hazard ................................................................................................................... 30

Figure 3-11 Mine Subsidence Districts ............................................................................................................. 32

Figure 3-12 Existing and predicted settlement lines ........................................................................................ 33

Figure 3-13 Observed vs predicted surface settlement, tilt and strain reading above Longwalls 11 to 18 of

West Wallsend Colliery ........................................................................................................... 33

Figure 3-14 Areas of former underground mine working and surface access points (SLR 2016) ................... 35

Figure 3-15 Available geotechnical locations ................................................................................................... 37

Figure 5-1 Slope stability risk mapping ............................................................................................................ 48

Figure 5-2 Slope stability risk mapping (geo zones) ........................................................................................ 49

Figure 5-3 Geology risk mapping (geo zones) ................................................................................................. 50

Figure 5-4 Depth of regolith risk mapping ........................................................................................................ 51

Figure 5-5 Soil landscapes risk mapping ......................................................................................................... 52

Figure 5-6 ASS risk mapping ............................................................................................................................ 54

`

### Geotechnical Report Page 5

`

Figure 5-7 Overall salinity risk mapping ........................................................................................................... 55

Figure 5-8 Near surface geotechnical constraints map .................................................................................... 58

Figure 5-9 Cross sections of the TSF storage (ATC Williams, 2025) .............................................................. 60

Figure 5-10 Section of eastern embankment area (ATC Williams, 2025) ........................................................ 60

Figure 5-11 Section of eastern embankment area (ATC Williams, 2025) ........................................................ 60

Figure 7-1 Potential initial developable areas around eastern edge of TSF (blue) .......................................... 72

Tables

Table 2-1 Sub-precinct references ..................................................................................................................... 5

Table 3-1 Sub-precincts description and topography across the MCC site ....................................................... 9

Table 3-2 Historical land use observations (1953 to 2026) .............................................................................. 12

Table 3-3 Regional geology – stratigraphy, lithology and unit characteristics and typical limitations .............. 17

Table 3-4 Expected geology and areas of disturbed terrain across the sub-precincts .................................... 18

Table 3-5 Depth of regolith and anticipated soil profiles across the sub-precincts .......................................... 20

Table 3-6 Slope stability geo zones ................................................................................................................. 22

Table 3-7 Geo zones across the Structure Plan sub-precincts ........................................................................ 23

Table 3-8 Soil landscapes - topography, soil characteristics and typical limitations ........................................ 25

Table 3-9 Expected soil landscapes and key limitations across the sub-precincts .......................................... 27

Table 3-10 ASS probability across the sub-precincts ...................................................................................... 28

Table 3-11 Overall salinity hazard across the sub-precincts ............................................................................ 30

Table 3-12 Mine subsidence hazard across the sub-precincts ........................................................................ 35

Table 3-13 Summary of existing geotechnical information within or adjacent to the MCC Precinct ................ 38

Table 3-14 Summary of existing geotechnical information within or adjacent to Teralba Southgate .............. 40

Table 4-1 Expected ground models across the sub-precincts ......................................................................... 43

Table 5-1 Summary of constraint categories and associated datasets ........................................................... 46

Table 5-2 Geotechnical constraints risk ranking criteria .................................................................................. 47

Table 5-3 Slope stability criterion and weighting for near surface geotechnical constraint mapping ............... 48

Table 5-4 Overall slope stability risk ranking for each sub-precinct ................................................................. 48

Table 5-5 Slope stability criterion and weighting for near surface geotechnical constraint mapping (geo

zones) ..................................................................................................................................... 49

Table 5-6 Overall slope stability risk ranking for each sub-precinct (geo zones) ............................................. 49

Table 5-7 Geology criterion and weighting for near surface geotechnical constraint mapping ....................... 50

Table 5-8 Overall geology risk ranking for each sub-precinct .......................................................................... 51

Table 5-9 Depth of regolith criterion and weighting for near surface geotechnical constraint mapping .......... 52

Table 5-10 Overall depth of regolith risk ranking for each sub-precinct ........................................................... 52

Table 5-11 Soil landscapes criterion and weighting for near surface geotechnical constraint mapping.......... 53

Table 5-12 Overall soil landscapes risk ranking for each sub-precinct ............................................................ 54

Table 5-13 ASS criterion and weighting for near surface geotechnical constraint mapping ............................ 54

Table 5-14 Overall ASS risk ranking for each sub-precinct ............................................................................. 55

Table 5-15 Salinity criterion and weighting for near surface geotechnical constraint mapping ....................... 55

Table 5-16 Overall salinity risk ranking for each sub-precinct .......................................................................... 56

Table 5-17 Near surface geotechnical risk ranking per sub-precinct ............................................................... 57

Table 5-18 Overall risk ranking within the TSF area (for reference only) ........................................................ 59

Table 7-1 Sub-precinct land use intents and anticipated structural characteristics ......................................... 63

Table 8-1 Summary of recommendations ........................................................................................................ 73

`

### Geotechnical Report Page 6

`

Project number 531168-000  File Geotechnical Engineering Report Rev B_Clean.docx  2026-07-01  Revision B

1

Definitions and abbreviations

Abbreviation

Definition

ASS

Acid Sulfate Soils

CFA

Continuous Flight Auger

CSIRO

Commonwealth Scientific and Industrial Research Organisation

EbD

Enquiry by Design

GIS

Geographic Information System

m AHD

metres Australian Height Datum

m BGL

metres Below Ground Level

MCC

Macquarie Coal Complex

PLMU

Post Mining Land Use

RL

Reduced Level

TSF

Tailings Storage Facility

SA

Subsidence advisory

WBH

West Borehole

YW

Young Wallsend

`

### Geotechnical Report Page 7

`

Project number 531168-000  File Geotechnical Engineering Report Rev B_Clean.docx  2026-07-01  Revision B

2

1

Executive summary

This Geotechnical Engineering Report has been prepared to support the State-led rezoning of the Macquarie

Coal Complex (MCC) (the Precinct), and Teralba Southgate for post-mining land use. The report provides a

precinct-scale assessment of geotechnical conditions, constraints and risks, and establishes a risk-informed

framework to guide land use planning, infrastructure provision, and staging.

The Precinct and Teralba Southgate comprises a highly modified post-mining landscape characterised by

variable topography, anthropogenic ground conditions, and legacy mining impacts, including mine

subsidence risk, disturbed terrains, a Tailings Storage Facility (TSF) and areas of potentially deep alluvium.

These conditions result in spatially variable development constraints across the Precinct and Teralba

Southgate.

A multi-criteria geotechnical assessment has been undertaken, considering slope, geology, regolith depth,

soil landscapes, groundwater, salinity and acid sulfate soils. The assessment identifies a range of

constraints, from low to high, across the Precinct and Teralba Southgate and confirms that development

feasibility will depend on location, land use intensity and staging.

1.1

Key geotechnical constraints

The principal geotechnical constraints affecting the Precinct and Teralba Southgate include:

 Mine subsidence: all the sub-precincts are underlain by historic underground coal workings, resulting in

potential subsidence risk that must be considered in land use planning and foundation design. Potential

subsidence risks are not currently quantified as further studies are required. Development in these areas

must include geotechnical assessments to characterise the risk and potentially solutions such as grouting

of the former workings, if settlement has not already occurred.

 Tailings Storage Facility: the TSF comprises hydraulically placed tailings and fill materials with high

variability, uncertain composition, and long-term settlement potential. The area is currently undergoing

rehabilitation and remains a declared dam. It represents a high-risk area for development, with settlement

potentially occurring over decades.

 Alluvial and low-lying areas: land adjacent to Cockle Creek and its tributaries is characterised by deep,

compressible soils, shallow groundwater, flooding and acid sulfate soil risk, presenting significant

constraints to structural development.

 Disturbed and anthropogenic terrains: areas of fill and disturbed ground exhibit variable and uncertain

geotechnical properties, reducing bearing capacity and increasing settlement risk.

 Salinity and reactive soils: much of the Precinct and Taralba Southgate are affected by moderate to very

high salinity hazard and reactive clay soils, with implications for durability of infrastructure and long-term

maintenance.

1.2

Structure Plan sub-precincts and Teralba Southgate

 Lower constraint areas (e.g. Killingworth, West Lake, Teralba Southgate, Barnsley West and more

broadly the eastern portion of Cockle Creek) are suitable for early-stage development.

 Moderate constraint areas (e.g. environmentally constrained areas) require targeted investigation and

design responses prior to development, subject to subsidence risk investigation.

 Higher constrained areas, including the TSF within the Cockle Creek sub-precinct and floodplain

environments, are subject to long-term considerations for development potential.

Given that all the sub-precincts are likely underlain by historic underground mine workings and the entirety of

the Precinct and Terlaba Southgate is mapped as a declared Mine Subsidence District, all future

development will require approval from Subsidence Advisory NSW (SA) and may entail further site specific

mine subsidence investigations and assessments.

`

### Geotechnical Report Page 8

`

Project number 531168-000  File Geotechnical Engineering Report Rev B_Clean.docx  2026-07-01  Revision B

3

1.3

Infrastructure and constructability

The Report identifies several implications for infrastructure design:

 Flood-prone areas require resilient design and scour protection

 Ground improvement (e.g. preloading, wick drains) may be required in soft or compressible soils

 Excavation in coal-bearing strata may require selective removal and treatment

 Utilities may require specialised trenching, dewatering, and corrosion protection

These factors will influence development cost, timing and feasibility across the Precinct and Teralba

Southgate.

1.4

Data gaps and further investigations

The assessment identifies data limitations, including:

 Limited and dated geotechnical investigations

 Incomplete understanding of TSF material properties and depth

 Uncertainty in mine subsidence risks in details and condition of historic fill areas as well as groundwater

behaviour.

To address these uncertainties, following rezoning, further site-specific investigations are required to:

 Confirm ground conditions and groundwater regimes

 Refine geotechnical risk mapping

 Support detailed design and future development approvals.

Development at later stages must be supported by intrusive investigations, modelling, and engineering

validation.

In general, from a geotechnical perspective, the majority of the Precinct  is considered to be suitable for the

purposes of commercial and industrial use, with varying levels of localised mitigation measures based on

geographically specific constraints.

Referral to Subsidence Advisory NSW (SA NSW) will be required to confirm site specific requirements and

more detailed subsidence modelling may be required. It is expected that many of the site constraints can be

managed through engineering intervention such as ground improvement and consideration of mine

subsidence in structural design or ground stabilisation by means such as grouting of former workings.

`

### Geotechnical Report Page 9

`

Project number 531168-000  File Geotechnical Engineering Report Rev B_Clean.docx  2026-07-01  Revision B

4

2

Introduction

This Geotechnical Engineering Report (this Report) has been prepared by Aurecon on behalf of the

Department Planning, Housing and Infrastructure (DPHI) to support the State-led rezoning of the Macquarie

Coal Complex for Post Mining Land Use. The Macquarie Coal Complex Land Transformation Precinct (the

Precinct) and Teralba Southgate form part of the NSW Government’s investigation into future land use

pathways for mining affected land.

This Report provides a desktop based geotechnical assessment to support the rezoning, planning and

staged redevelopment of the Precinct and Teralba Southgate sub-precinct. It establishes an evidence base

to identify, assess and manage geotechnical constraints, and to guide investigation, earthworks and

foundation design requirements across in these areas.

The Report is intended to inform:

 State-led rezoning processes

 Structure planning and sub‑precinct development strategies

 Infrastructure planning and delivery

 Future development applications and site-specific investigations.

The Precinct and Teralba Southgate are characterised by a highly variable ground environment, shaped by:

 Underground mining (West Wallsend Colliery)

 Open cut mining and backfilled voids

 Coal processing infrastructure and tailings deposition

 Progressive rehabilitation and landform recontouring

These legacy conditions result in a range of geotechnical challenges, including:

 Mine subsidence risk

 Variable and uncontrolled fill

 Soft and compressible alluvial soils

 Groundwater variability

 Stability and settlement considerations associated with the Tailings Storage Facility (TSF).

A strategic, risk-informed framework to manage constraints associated with the geotechnical conditions of

the Precinct and Teralba Southgate should therefore be adopted.

2.1

Background

Open cut and underground mining operations have all ceased and current activities are focused on

rehabilitation, closure planning, and long-term environmental management.

The Macquarie Coal Complex is a decommissioned mining operation previously operated by Glencore,

which processed coal sourced from the nearby underground West Wallsend Colliery and the Westside open-

cut mining operations. Mining activities at West Wallsend Colliery, Westside open-cut mining operation and

Teralba Southgate respectively ceased in 2016, 2012 and 2001.

The Structure Plan has divided the Precinct and Teralba Southgate into three post mining land use land

categories for conservation, development and recreation purposes, further divided into six sub-precinct areas

as shown Figure 2-1 and listed in Table 2-1.

`

### Geotechnical Report Page 11

`

Project number 531168-000  File Geotechnical Engineering Report Rev B_Clean.docx  2026-07-01  Revision B

6

This Report has been prepared using publicly available information together with existing project data,

including previous geotechnical investigations, borehole logs, laboratory testing records, mine rehabilitation

documentation, and available topographic and subsidence information.

Specifically, the Report aims to:

 Provide a rezoning/master plan level geotechnical evidence base to verify developable land and inform

land use compatibility, built form intensity and infrastructure feasibility

 Translate Enquiry by Design (EbD) identified constraints, including soils, steep terrain constraints and

mine subsidence district considerations, into Master Plan mapping, performance criteria and staging

triggers

 Provide a clear pathway for later-phase investigations (intrusive testing, stability modelling, settlement

monitoring) without duplicating Development Application (DA) stage work.

2.3

Assumptions and limitations

This Report has been prepared to inform a Master Plan for post mining land use at the rezoning stage.  The

assessment is based on existing available information and does not constitute a DA level geotechnical

design assessment.

The following limitations apply to this assessment:

 This assessment has been limited to publicly accessible data available to Aurecon and that provided by

DPHI, and Glencore

 No geotechnical or hydrogeological modelling has been undertaken for the purpose of this assessment

 No detailed development analysis has been undertaken as part of geotechnical assessment

 No geotechnical investigations were carried out for this assessment.

The following items are specifically excluded from, or deferred beyond, the scope of this assessment:

 Comprehensive intrusive site investigation campaigns across the full Precinct and Teralba Southgate

 Detailed stability modelling, settlement predictions and foundation design

 DA stage geotechnical design certification and construction-phase verification

 Detailed data gaps identified for the geotechnical constraint assessment are further outlined in Section

5.2

 Mine subsidence is assumed to apply across the entire Precinct and Teralba Southgate, and is treated as

a site-wide constraint rather than a differentiating factor between sub-precincts.

`

## 4. Contamination, TSF & Dams

### Contamination Report Page 3

`

Project number 531168-000  File MCC PMLU Rezoning_Package B_Contamination Report_Final.docx  2026-07-01  Revision B

Executive summary

This Contamination Technical Assessment (CTA) has been prepared by Aurecon Australasia Pty Ltd

(Aurecon) on behalf of the Department of Planning, Housing and Infrastructure (DPHI) to support the State-

led rezoning of the Macquarie Coal Complex (the Precinct) and Teralba Southgate, located approximately 20

km southwest of Newcastle within the Lake Macquarie region, NSW.

The purpose of this CTA is to reinterpret existing contamination data, originally collected to support mine

closure and rehabilitation, within the context of proposed rezoning and future land use scenarios identified in

the Structure and Master Plan and Teralba Southgate. The assessment is scoped at the rezoning stage to

inform land use compatibility and identification of developable land. It does not constitute development

application (DA) level investigation or detailed remediation design.

Site Context

The Precinct comprises four former mining operations: including West Wallsend Colliery, Macquarie Coal,

Preparation Plant, Westside Mine (open-cut), and Teralba Colliery (Northgate). Teralba Southgate is located

approximately 2.5 kilometres south of the Precinct and is occupied by former mine infrastructure including

shafts. Mining activities ceased progressively between 2001 and 2016. Current activities are limited to

environmental management and rehabilitation in accordance with the Rehabilitation Management Plan (RMP

2022). The Precinct and Teralba Southgate are surrounded primarily by residential and mixed-use industrial

areas.

The rezoning aims to facilitate employment-led development supported by residential, conservation, and

open space land uses. A figure showing the extent of Teralba Southgate and the current Structure Plan for

the Precinct is provided in Figure E1.

Figure E1 – Layout and extent of Teralba Southgate and the Structure Plan for the Precinct

`

### Contamination Report Page 5

`

Project number 531168-000  File MCC PMLU Rezoning_Package B_Contamination Report_Final.docx  2026-07-01  Revision B

Figure E2 – Location and extent of the closure domains at the Precinct and Teralba Southgate

Data Gaps and Limitations

Significant data gaps limit ability for full characterisation of contamination and land suitability, including:

◼ Multiple domains with no intrusive investigation (lacking soil, groundwater, surface water and sediment

data).

◼ Incomplete ASS and groundwater characterisation.

◼ Limited assessment beneath buildings and inaccessible areas/structures.

◼ Incomplete delineation of buried asbestos materials.

◼ Limited ground gas assessments.

Land Use Suitability

Based on available data and acknowledging limitations:

◼ Commercial and industrial uses - Generally compatible across most of the Precinct and Teralba

Southgate, subject to targeted investigation and management.

◼ Sensitive uses (residential, conservation, recreational) - Require further investigation and risk assessment

to confirm suitability.

◼ Key constraint - The Tailings Storage Facility (Domain 7) presents a significant constraint requiring

detailed, multidisciplinary assessment.

`

### Contamination Report Page 6

`

Project number 531168-000  File MCC PMLU Rezoning_Package B_Contamination Report_Final.docx  2026-07-01  Revision B

Implementation Approach and Key Recommendations

A staged, risk-based approach to investigation and management is recommended to support rezoning and

future development. With appropriate controls and management (including detailed site investigations and

appropriate remediation), the Precinct and Teralba Southgate can be made suitable for its intended uses

while protecting human health and environmental values, including Cockle Creek and Lake Macquarie.

Based on available data and with consideration to identified data gaps, the assessment concludes that

known or potential contamination is unlikely to preclude commercial/industrial rezoning for the majority of the

Precinct and Teralba Southgate, provided that targeted investigation and appropriate management controls

are implemented during future design and construction phases.  However, suitability determinations vary by

sub-precinct and proposed land use. Employment-led commercial and industrial uses are generally

considered compatible with the current contamination profile across most sub-precincts. However, more

sensitive land uses including medium or high-density residential, conservation, and recreational uses,

require targeted investigation and risk assessment to confirm suitability. This is particularly important at

Teralba Southgate where detailed ground gas assessments have not been undertaken. The Tailings Storage

Facility (Domain 7) also represents a material constraint requiring detailed assessment and integrated

management across multiple environmental and engineering disciplines.

Implementation of the management framework and performance criteria outlined in this CTA, combined with

progressive investigation and remediation through the DA approval process, will enable the Precinct and

Teralba Southgate to support sustainable post-mining land use while protecting human health and

environmental values in Cockle Creek and Lake Macquarie.

Based on the findings of this assessment, and subject to the limitations outlined in Section 11, Aurecon

presents the following recommendations:

◼ Implement a risk-based, staged investigation program for all future development proposals, with Detailed

Site Investigations (DSIs) and Tier 2/3 quantitative risk assessments undertaken where elevated COPC

concentrations are present or data gaps are identified, ensuring land use suitability is confirmed prior to

development approval

◼ Prioritise targeted investigation of Domains 2, 5, 7, 14, and 16 (uninvestigated domains), comprehensive

groundwater assessment across all domains, ASS characterisation in low-lying areas, and asbestos

delineation sampling to resolve material data gaps constraining sensitive land use suitability

determination

◼ Undertake integrated assessment of the Tailings Storage Facility (TSF) across water management,

geotechnical stability, dam safety, and regulatory compliance frameworks, including geochemical

characterisation of tailings materials and assessment of leachate generation and Acid Mine Drainage

(AMD) pathways to inform remediation and long-term management strategy

◼ Undertake targeted surface water and sediment quality assessments adjacent to waterway and wetland

interface zones (including recreational areas within West Lake); and assess PFAS-impacted areas in

accordance with the PFAS National Environmental Management Plan (NEMP 3.1)

◼ Undertake comprehensive ground gas assessment in accordance with NSW EPA Assessment and

management of hazardous ground gases (EPA 2020), with particular focus on Domains 11 and 13 where

methane concentrations were reported. If required, implement ground gas mitigation measures during

building design and construction to prevent vapour intrusion risk to future enclosed structures

◼ Confirm land suitability for more sensitive uses (residential in Teralba Southgate, conservation, and

recreational uses) through targeted investigation of soil, groundwater, surface water, and ground gas;

implement PFAS plume delineation, asbestos delineation, and methane management measures; obtain

Site Audit Statements from NSW EPA-accredited Site Auditors where remediation or management

measures are implemented

◼ Implement contamination pathway controls during earthworks and future development to prevent

migration of identified COPCs to Cockle Creek and Lake Macquarie

◼ Ensure all contamination assessments comply with NSW EPA Guidelines and are prepared by a suitably

qualified contaminated land consultant including any review and update of duty to report obligations under

Section 60 of the Contaminated Land Management Act 1997 at each DA-stage investigation and

`

### Contamination Report Page 7

`

Project number 531168-000  File MCC PMLU Rezoning_Package B_Contamination Report_Final.docx  2026-07-01  Revision B

preparation of Long-Term Environmental Management Plans (LTEMPs) where residual contamination

risks remain. As per Lake Macquarie City Council’s (LMCCs) requirements, an EPA certified consultant

must be engaged where reports are submitted to the NSW EPA or where required by the consent

authority

◼ All future works should be conducted by an appropriately qualified environmental consultant under the

direction of a CEnvP-SC or equivalent accreditation. An accredited NSW EPA Auditor may be required to

endorse the investigation, remediation/management and validation works where more sensitive land uses

are proposed or where there are elevated risks to ecological receptors.

Pathway for Residential Development (Teralba Southgate)

Residential development at Teralba Southgate will require a standard but targeted contaminated land

assessment and approval process, including:

◼ Detailed Site Investigation (DSI) involving intrusive assessment to fully characterise the nature and extent

of contamination across the site in potentially affected media (i.e. ground gas and to a lesser extent soil,

groundwater, surface water, sediment) with data comparison made to applicable land use criteria as per

the NEPM (e.g. medium to high density residential).

◼ Remedial Action Plan (RAP) to define extents and media requiring remediation and/or management to

render the site suitable for the proposed land uses (e.g. residential).

◼ Validation sampling and reporting to confirm remediation objectives have been achieved.

◼ Independent Site Audit by an accredited NSW EPA Auditor which is recommended for residential land

use on a former mine site, to provide independent assurance of site suitability prior to development

consent being granted.

This process will demonstrate that the land is suitable, or can be made suitable, for residential use in

accordance with the NEPM (2013), EP&A Act, State Environmental Planning Policy (SEPP, Resilience and

Hazards) 2021 and relevant NSW EPA legislation and guidelines.

`

### Contamination Report Page 8

`

Contents

Executive summary ........................................................................................................................................... i

1 Introduction .................................................................................................................................................. 1

1.1

Introduction ............................................................................................................................... 1

1.2

Objectives ................................................................................................................................. 1

1.3

Methodology ............................................................................................................................. 2

2 Planning context and limitations ............................................................................................................... 3

2.1

Level of detail and exclusions .................................................................................................. 3

2.2

Reliance on data and information ............................................................................................. 3

3 Baseline analysis ........................................................................................................................................ 5

3.1

Environmental setting ............................................................................................................... 5

3.2

Areas of Environmental Concern ............................................................................................. 6

3.3

Summary of Previous Investigations ........................................................................................ 7

3.4

Previous Remediation Activities ............................................................................................... 8

3.5

Data gaps ................................................................................................................................. 8

4 Conceptual Site Model ................................................................................................................................ 9

4.1

Sources, pathways, and receptors ........................................................................................... 9

4.2

Domain Constraints Analysis ................................................................................................... 9

4.2.1

Consequence qualification ........................................................................................ 9

4.2.2

Likelihood qualification ............................................................................................ 10

4.3

Constraint determination ........................................................................................................ 11

4.4

Preliminary conceptual site model .......................................................................................... 11

5 Land Use Capability .................................................................................................................................. 16

5.1

Sub precinct 1 – Cockle Creek ............................................................................................... 16

5.2

Sub precinct 2 – Killingworth .................................................................................................. 17

5.3

Sub precinct 3 – West Lake ................................................................................................... 17

5.4

Teralba Southgate .................................................................................................................. 18

5.5

Sub precinct 5 – Barnsley West ............................................................................................. 19

5.6

Sub precinct 6 –Environmentally Sensitive Areas .................................................................. 19

5.6.1

Sub precinct 6a ........................................................................................................ 19

5.6.2

Sub precinct 6b ........................................................................................................ 19

5.6.3

Sub precinct 6c ........................................................................................................ 20

5.6.4

Sub precinct 6d ........................................................................................................ 20

5.6.5

Sub precinct 6e ........................................................................................................ 20

5.6.6

Sub precinct 6f ......................................................................................................... 21

5.7

Interfaces with other constraints ............................................................................................. 21

5.7.1

Waterways and Wetlands ........................................................................................ 21

5.7.2

Acid Sulfate Soils..................................................................................................... 21

5.7.3

Salinity ..................................................................................................................... 22

5.7.4

Tailings Storage Facility .......................................................................................... 22

5.7.5

Earthworks and Spoil Management ........................................................................ 22

5.7.6

Water Reuse Concepts ........................................................................................... 23

5.7.7

Ground Gas ............................................................................................................. 23

6 Master Plan objectives and performance criteria .................................................................................. 24

6.1

Contamination Master Plan Objectives .................................................................................. 24

6.2

Contamination Performance Criteria ...................................................................................... 25

`

### Contamination Report Page 9

`

7 Investigation and remediation triggers ................................................................................................... 27

8 Post exhibition management framework and approvals pathway ....................................................... 29

8.1

Development application ........................................................................................................ 29

8.2

Regulatory notifications and duty to report ............................................................................. 29

8.3

Opportunities .......................................................................................................................... 30

9 Conclusions and recommendations ....................................................................................................... 31

9.1

Conclusions ............................................................................................................................ 31

9.2

Recommendations.................................................................................................................. 32

10 References ................................................................................................................................................. 33

11 Limitations ................................................................................................................................................. 35

B-1. Detailed summary of investigations undertaken at each Domain ............................................... 39

B-2. Summary of Acid Sulfate Soil and Salinity Assessment Data ..................................................... 44

Appendices

Appendices

Appendix A – Figures

Appendix B – Previous investigations summary

Appendix C – Summary of Data Gaps

Appendix D – Domain risk qualifications

Tables

Table 3-1 Summary of Environmental Setting

Table 3-2 Summary of AECs (Closure Domains) across the Precinct and Teralba Southgate.

Table 3-3 Summary of previous remediation activities

Table 4-1 Summary of key CSM components

Table 4-2 Consequence qualifications and ratings

Table 4-3 Domain constraint determination matrix

Table 4-4 Preliminary CSM for the Precinct and Teralba Southgate

Table 6-1 Master Plan Objectives

Table 6-2 Summary of Performance Criteria

Table 7-1 Investigation and Remediation Triggers

Table 11-1 Summary of Data Gaps

Table 11-2 Domain constraint rating qualifications

`

### Contamination Report Page 10

`

Project number 531168-000  File MCC PMLU Rezoning_Package B_Contamination Report_Final.docx  2026-07-01  Revision B

1

1

Introduction

1.1

Introduction

Aurecon Australasia (Aurecon) was engaged by the Department of Planning, Housing and Infrastructure

(DPHI) for a variety of engineering services to support the State-led rezoning of the Macquarie Coal

Complex, herein referred to as “the Precinct” and “Teralba Southgate”. The Precinct and Teralba Southgate

are located approximately 20 kilometres (km) southwest of Newcastle, in the Lake Macquarie region of New

South Wales (NSW). It is noted that Teralba Southgate has been removed from the scope of the Master Plan

and will not be pursued under a State Environmental Planning Policy (SEPP) rezoning process. Instead,

Teralba Southgate is proposed to be rezoned under a Local Environmental Plan (LEP). A figure showing the

location and extent of the Precinct and Teralba Southgate is provided in Figure 1, Appendix A.

The Precinct encompasses the former West Wallsend Colliery (WWC), the Macquarie Coal Preparation

Plant (MCPP), the former open-cut Westside Mine, and the former Teralba Colliery (Northgate site). Mining

operations ceased progressively across the Precinct, with Teralba Colliery closing in 2001, Westside Mine

ceasing operations in 2012, and West Wallsend Colliery and Macquarie Coal Preparation Plant concluding

operations in 2016.Current activities are focused on long-term environmental management and rehabilitation

in accordance with the Rehabilitation Management Plan (RMP 2022).

This Contamination Technical Assessment (CTA) builds on the Post Mining Land Use Engineering Analysis

Report (Aurecon 2026) and has been developed to support refinement of the Master Plan and to inform

DPHI's decision making as part of the rezoning process. It is noted that environmental and contamination

investigations completed to date have been undertaken primarily to support mine closure obligations, rather

than to establish suitability for alternative land uses. Accordingly, this assessment reinterprets existing

contamination data within the context of the proposed rezoning and future land use scenarios shown in

Figure 2, Appendix A.

1.2

Objectives

The objective of this CTA is to support refinement of the Master Plan and to inform DPHI's decision making

as part of the rezoning process. Specifically, the objectives of this CTA are to:

◼ Provide a precinct-scale contaminated land evidence base to support rezoning and Master Plan land use

compatibility, building on existing contamination assessments referenced through Enquiry by Design

(EbD) engineering discussions

◼ Confirm whether contamination represents a material constraint to developable land verification for

employment-led uses and identify where more sensitive land uses would require additional evidence and

management

◼ Translate contamination findings into Master Plan-ready objectives, performance criteria and a clear

staged investigation/remediation pathway to be implemented post rezoning.

`

### Contamination Report Page 11

`

Project number 531168-000  File MCC PMLU Rezoning_Package B_Contamination Report_Final.docx  2026-07-01  Revision B

2

1.3

Methodology

The scope of this CTA comprises five integrated components to achieve the rezoning objectives including:

◼ Desktop compilation including a review and synthesis of previous investigations and assessment

documents

◼ Systematic constraints analysis including the identification of Areas of Environmental Concern (AECs)

and assessment of remediation implications under different land use scenarios

◼ Development of a Conceptual Site Model (CSM) to integrate source pathway receptor (SPR) linkages

across the Precinct and Teralba Southgate

◼ Identification of data gaps to inform recommendations for future investigation

◼ Development of a management framework to integrate contamination management into the future

planning and development approval pathway, including staged investigation triggers, regulatory

notification protocols, and interfaces with other engineering and environmental disciplines.

`

## 5. Economic & Market Assessment

### Economics Report Page 5

`

5

Executive summary

Lake Macquarie City Council engaged Aurecon to undertake an economic, social and market assessment of

redevelopment opportunities for the Macquarie Coal Complex (Precinct) and Teralba Southgate, collectively referred

to as the “Site”. The assessment has been undertaken to provide an evidence base for future land use decision-making

as the Site transitions through closure and rehabilitation towards productive post-mining uses. This report ("Package

E") brings together baseline demographic, labour market, economic, social and market evidence to support the Master

Plan process. It tests the land use directions emerging from the Enquiry by Design process and considers their

feasibility, economic contribution, social implications, market readiness, risks and dependencies.  The assessment is

prepared for an early planning and pre-investment context. It provides a structured evidence base to support land use

decision-making, future business case development and further technical testing.

Market assessment and land use opportunities for employment

The Site's scale, industrial legacy, proximity to established communities, access to regional labour markets and

potential infrastructure links favour employment-generating uses. The land use opportunities are grouped into three

categories. Table 0-1 summarises land use opportunities by priority, time horizon and employment.

Table 0-1: Market assessment summary of potential post-mining land uses1

Land use

Priority

Time horizon

Employment

generation (ongoing)

Key opportunities

Circular

economy,

industrial and

advanced

manufacturing

High

Near term

(0–5 years)

Up to 40 jobs per

facility2

Integrated circular economy; precision

fabrication; advanced industrial and

manufacturing uses.

Waste and

resource

recovery

High

Near term

(0–5 years)

Up to 100 jobs per

facility

Accumulating feedstock for circular

economy and manufacturing, e.g.

Recycling and e-waste facilities.

Energy transition

and renewable

infrastructure

High

Near-long

term

(0–5 years)

Up to 20 jobs per

facility

Battery energy storage systems (BESS)

and related energy infrastructure.

Freight,

logistics,

distribution and

supply chain

hub

Conditional

Long term

(15+ years)

Up to 400 jobs per

facility

Expansion of logistics and transport

operations; e-commerce hub; cold

chain and perishable goods logistics.

Data centres

and digital

infrastructure

Conditional

Medium-long

term

(10–15 years)

Up to 50 jobs per

facility

Data storage centres supporting cloud

and enterprise clients; small-scale

facilities for regional data processing.

Community,

tourism and

agriculture

Conditional

Near-medium

term

(5–10 years)

Up to 130 jobs per

facility

Open spaces; visitor economy and

eco-tourism; cultural experiences; and

controlled environment agriculture.

Residential

Complemen-

tary

Near-medium

term

(5–10 years)

Up to 50 jobs per

facility3

Residential development and senior

living.

Education,

research and

innovation

Optional

Long term

(15+ years)

Not assessed for

optional land use

Clean technology innovation hub;

energy transition training and

workforce development centres.

1 Note: Excludes construction jobs.

2 Up to 40 jobs per facility, noting that these will use more robotics than traditional manufacturing.

3 Note: Applies to Senior Living facilities.

`

### Economics Report Page 6

`

6

The categories above reflect the relative readiness and strategic role of each land use within the Site, having regard to

market demand, alignment with site attributes, infrastructure and servicing requirements, and the extent of further

investigation and delivery planning required. These are defined below:

▪ Highly feasible: circular economy, industrial and advanced manufacturing, waste and resource recovery, and

energy transition infrastructure and renewables. These uses have near-term feasibility, alignment with the

Site's scale, industrial legacy and workforce. They can proceed earliest and anchor investment.

▪ Conditional: freight and logistics, data centres, and community, tourism and agriculture. These uses have

strategic merit but depend on conditions being met first, principally infrastructure capacity, market maturity,

anchor tenants and policy support. They are sequenced to later horizons as those conditions are resolved.

▪ Complementary: residential uses support the Site's function, liveability and public benefit but are not the

primary economic drivers.

The Site’s key opportunity lies in its flexibility to accommodate a range of employment-generating, infrastructure-led

and complementary uses as market, infrastructure and policy conditions evolve. In total, these uses have the

potential to support around 1,130 ongoing jobs.

Social implications and consideration for land use

▪ Minimising social impacts and sustaining social outcomes will depend on how effectively economic benefits

are accessed, shared and supported over time.

▪ Transport access is the key consideration across all land uses. Limited public transport accessibility will

reduce future access to jobs and services, particularly for lower-income households, older residents, people

with disabilities and those without private vehicles.

▪ Employment-generating uses (freight, logistics, data centres) offer strong economic potential but introduce

trade-offs such as increased traffic, amenity impacts and pressure on local services. Industrial and circular

economy uses align with regional transition objectives, but their social outcomes depend on how well impacts

are managed and local workforce pathways are enabled.

▪ Complementary uses (community infrastructure, housing, recreation, health services) are likely to deliver

more direct social benefits, supporting liveability, wellbeing and place identity.

▪ Cumulative impacts from workforce growth, concurrent regional activity, and construction and operational

phases will increase demand for housing and services and require coordinated planning.

▪ Social outcomes can be strengthened through improved transport access, local employment pathways,

Aboriginal participation and community benefit sharing.

Key concluding considerations and next steps

▪ The Site has credible potential to contribute to Lake Macquarie's economic transition and employment land

supply and is not immediately market-ready for all uses. Success will depend on staged de-risking, clear

planning pathways, infrastructure sequencing, targeted market testing and land use flexibility.

▪ The social findings highlight key considerations which require careful planning, further investigation and

engagement with the community. Future decisions should not weigh only on the number of jobs or scale of

investment, but whether benefits are accessible, locally captured and supported by housing, transport, social

infrastructure and biodiversity outcomes.

▪ This assessment recommends a pragmatic approach to prioritise feasible employment-generating uses

and protect longer-term optionality.

▪ Advance to Business Case development for high priority near term uses, building on this assessment

through refined technical studies, commercial analysis, and stakeholder validation to support an informed

investment decision.

`

### Economics Report Page 7

`

7

Contents

Disclaimer ....................................................................................................................................................... 3

Executive summary .......................................................................................................................................... 5

Part A: Land use assessment ............................................................................................................................ 1

1

Introduction and background................................................................................................................ 2

1.1

Project overview ................................................................................................................................... 2

1.2

Lake Macquarie's strategic role in regional transition economy ............................................................ 3

1.3

Purpose and scope of this report .......................................................................................................... 5

1.4

Relationship to other technical packages ............................................................................................. 6

2

Preliminary land use feasibility assessment .......................................................................................... 7

2.1

Land use feasibility assessment framework ......................................................................................... 7

2.2

Land uses identified for the Site ............................................................................................................ 8

2.3

Market opportunities for the Site......................................................................................................... 10

2.4

Opportunities for high feasibility land uses ......................................................................................... 13

2.4.1

Circular Economy, Industrial and Advanced Manufacturing ................................................ 13

2.4.2

Waste and Resource Recovery ............................................................................................ 17

2.4.3

Energy Transition and Renewable Infrastructure .................................................................. 18

2.5

Opportunities for conditional land uses .............................................................................................. 19

2.5.1

Data Centres and Digital Infrastructure ............................................................................... 19

2.5.2

Freight Logistics, Distribution and Supply Chain Hub .......................................................... 20

2.5.3

Community, Tourism and Agriculture .................................................................................. 22

2.6

Opportunities for complementary land uses....................................................................................... 24

2.6.1

Residential .......................................................................................................................... 24

2.7

Opportunities for optional land uses .................................................................................................. 25

2.7.1

Education, Research and Innovation Precinct ..................................................................... 25

2.8

Summary of employment opportunities.............................................................................................. 27

3

Post-mining impediments, reform consideration and social implications ............................................. 28

3.1

Regulatory and delivery framework assessment ................................................................................. 28

3.1.1

Assessment of key frameworks ........................................................................................... 28

3.1.2

Structural constraint typologies .......................................................................................... 30

3.2

Transition risks and mitigation strategies, and social considerations .................................................. 31

3.2.1

Land use dependencies and transition risks ........................................................................ 31

3.3

Overarching risks and strategies ......................................................................................................... 41

4

Social and community implications for delivery .................................................................................. 45

4.1

Other cumulative social impacts ........................................................................................................ 45

4.2

Summary of social implications and considerations ........................................................................... 46

4.3

Enabling options to create social benefits .......................................................................................... 47

4.4

Social considerations in economic terms ........................................................................................... 49

5

Key findings and recommendations .................................................................................................... 50

5.1

Key findings to support a flexible employment precinct ...................................................................... 50

5.1.1

Integrated land use and employment opportunities ............................................................ 51

5.2

Key recommendations........................................................................................................................ 52

5.3

Future business case development considerations ............................................................................ 53

`

### Economics Report Page 8

`

8

Part B: Detailed methodology ......................................................................................................................... 55

6

Methodology and assessment framework ........................................................................................... 56

6.1 Social and economic study areas............................................................................................................... 56

6.2 Analytical approach ................................................................................................................................... 57

6.3 Assumptions, exclusions, and dependencies ............................................................................................ 58

6.3.1 General assumptions ................................................................................................................. 58

6.3.2 Exclusions and dependencies .................................................................................................... 58

7

Strategic context and existing evidence .............................................................................................. 60

7.1 Overview of key studies and inputs ............................................................................................................ 60

7.2 Regional drivers influencing land use feasibility ......................................................................................... 61

8

Demographic, social and labour market analysis................................................................................. 63

8.1

Demographic profile ........................................................................................................................... 63

8.1.1

Population growth and change ............................................................................................ 63

8.2

Socio-economic vulnerability indicators ............................................................................................. 64

8.3

Community values and identity .......................................................................................................... 65

8.4

Areas of community interest ............................................................................................................... 67

8.5

Social infrastructure and transport context ........................................................................................ 68

8.5.1

Public transport provisions .................................................................................................. 71

8.5.2

Social infrastructure and public transport accessibility ....................................................... 72

8.6

Workforce characteristics .................................................................................................................. 72

8.6.1

Population and working age profile ...................................................................................... 73

8.6.2

Labour force participation ................................................................................................... 73

8.6.3

Skills and educational attainment ....................................................................................... 74

8.6.4

Workforce mobility and travel to work ................................................................................. 74

8.7

Economic and industry analysis ......................................................................................................... 75

8.7.1

Industry output and value-add ............................................................................................. 75

8.7.2

Labour market analysis ....................................................................................................... 76

8.7.3

Lake Macquarie employment projection.............................................................................. 78

8.8

Coal mining workforce profile ............................................................................................................. 78

8.8.1

Coal mining dependent employment profile ........................................................................ 79

8.8.2

Coal mining dependent workforce transition ....................................................................... 81

9

Appendices........................................................................................................................................ 84

Appendices

Appendix A: Analysis of economic contributions of land uses

Appendix B: Consultations with NZEA

Appendix C: Media scan

Appendix D: Policy and legislation scan

Appendix E: PTAL methodology

Appendix F: Detailed PTAL of social infrastructure facilities in the SSA

Appendix G: Data sources

Appendix H: Socio-economic vulnerability indicators

Appendix I: Key areas of community interest

Appendix J: Non-Indigenous heritage items

`

### Economics Report Page 9

`

9

Figures

Figure 1-1: Site context and Master Plan land use areas

Figure 1-2: Lake Macquarie LGA economic snapshot

Figure 2-1: Land use feasibility assessment framework

Figure 2-2: Land use priority mapping

Figure 2-3: Indicative categorisation of sub-precincts for the Site

Figure 3-1: The Site structural constraint typologies

Figure 6-1: Site social and economic study area

Figure 6-2: Analytical approach for the economic, social and market assessment

Figure 8-1: Demographic profile of the social and economic study areas,

Figure 8-2: Lake Macquarie LGA forecast population and year-on-year growth

Figure 8-3: Snapshot of Socio-economic vulnerability indicators,, ,

Figure 8-4: Map of all non-Indigenous heritage sites

Figure 8-5: Map of key areas of community interest in relation to the Site location.

Figure 8-6: Social infrastructure within SSA

Figure 8-7: Social infrastructure within 5km radius of the Site

Figure 8-8: PTAL and social infrastructure near the Site

Figure 8-9: SSA and ESA travel to work

Figure 8-10: Lake Macquarie LGA output by industry ($M)

Figure 8-11: Location Quotients of Lake Macquarie LGA and Change in Employment for the ten highest industries

Figure 8-12: Total Employment within the ESA and SSA

Figure 8-13: Projected change in Industry Employment in 2041 relative to 2026 across Lake Macquarie LGA

Figure 8-14: Work and residence characteristics of mining workforce in Lake Macquarie LGA

Figure 8-15: Number of coal mining dependent sector workers,, distributed by age for ESA and SSA

Figure 8-16: Spatial distribution of mining workers in the ESA

Figure 9-1: Framework principles for the government priorities land use tier system

Figure 9-2: Population age-distribution for SSA, ESA and NSW

Figure 9-3: Total income weekly across the SSA, ESA and NSW

Figure 9-4: SEIFA IRSD index within SSA

Tables

Table 0-1: Market assessment summary of potential post-mining land uses

Table 1-1: Macquarie Coal Complex Land Transformation Precinct technical packages

Table 2-1: Market opportunities for the Site

Table 2-2: Circular Economy, Industrial and Advanced Manufacturing market opportunities for the Site

Table 2-3: Waste and Resource Recovery market opportunities for the Site

Table 2-4: Energy Transition & Renewable Infrastructure market opportunities

Table 2-5: Data centres and digital infrastructure market opportunities

Table 2-6: Freight Logistics, Distribution & Supply Chain market opportunities for the Site

Table 2-7: Community, Tourism and Agriculture opportunities for the Site

Table 2-8: Residential opportunities for the Site

Table 2-9: Education, Research & Innovation market opportunities

Table 3-1: Post-mining site redevelopment enablement and reform considerations

Table 3-2: Key transition risks and mitigation strategies for the Site

Table 4-1: Cumulative social impacts

Table 4-2: Social considerations and implications

Table 4-3: Social benefits and opportunities

Table 4-4: Social findings in economic terms

Table 5-1: Integrated land use key findings

`

### Economics Report Page 10

`

10

Table 5-2: Indicative timeframe development scenario and recommended strategy

Table 5-3: Potential land use opportunities for future business case consideration

Table 6-1: Social versus economic study area

Table 6-2: Exclusions and dependencies of assessment

Table 7-1: Relevant studies and key findings

Table 7-2: Demand drivers of LGA

Table 8-1: Vulnerability indicators and planning implications

Table 8-2: Community values and identity overview

Table 8-3: Key community values and priorities

Table 8-4: Key areas of community interest within 5km of the Site

Table 8-5: key findings of social infrastructure and public transport access

Table 8-6: Social infrastructure facilities within the SSA and 5 km of the Site

Table 8-7: Public transport accessibility by area

Table 8-8: Public transport accessibility of social infrastructure facilities in the SSA

Table 8-9: Population by broad age group, SSA and ESA

Table 8-10: Total SSA and ESA labour force participation and employment (2021)

Table 8-11: Total SSA and ESA skills and educational attainment (2021)

Table 8-12: Number of jobs in the specified industry and change over time for SSA and ESA

Table 8-13: Occupational concentration within coal mining dependent workforce in the ESA (2021)

Table 9-1: 2023 CPAG workspace ratios and guidance

Table 9-2: Annual economic contribution from circular economy and advanced manufacturing uses

Table 9-3: Estimated direct economic contribution per annum from waste and resource recovery land use

Table 9-4: Annual economic contribution from energy transition infrastructure

Table 9-5: Direct operational impacts of data centres and digital infrastructure

Table 9-6: Annual economic contribution from freight, logistics and supply chain uses

Table 9-7: Estimated direct economic contribution per annum from community, tourism and agriculture land use

Table 9-8: Estimated direct economic contribution per annum from residential land use

Table 9-9: Land uses tier system based on government priorities

Table 9-10: Media scan and key points relevant to PLMU Sites throughout the SSA and ESA.

Table 9-11: State and local policy and legislation scan

Table 9-12: Data sources for the economic, social and market assessment

Table 9-13: Most advantaged and disadvantaged suburbs within the SSA and ESA

Table 9-14 Key areas of community interest

`

### Economics Report Page 12

`

2

1

Introduction and background

This Section focuses on project overview, Site, the purpose of the report, strategic alignment and relationship to other

packages.

1.1 Project overview

The Macquarie Coal Complex Pilot Project was initiated as part of the NSW Government’s wider response to the

Beneficial and productive post-mining land use Parliamentary Inquiry. 4  In July 2025 the NSW Government committed

to undertake two pilot projects to demonstrate how alternative post-mining land uses can be delivered under the

existing planning and regulatory framework.

The Macquarie Coal Complex Master Plan was prepared by the Department of Planning, Housing and Infrastructure

(DPHI) in partnership with Lake Macquarie City Council (Council), Net Zero Economy Authority (NZEA) and relevant

NSW Government agencies involved in post-mining land use, regional development and investment delivery. The

Department and Council have undertaken master planning informed by technical studies, to support the coordinated

transition of a former mine site to alternative employment generating land uses in the Precinct

The Rezoning Proposal applies to approximately 1,160 hectares of land which includes the Macquarie Coal Complex

Precinct and Teralba Southgate, collectively referred to as the “Site”.

The Precinct sits adjacent to the Lake Macquarie Northwest Catalyst Area.  It is bounded by the suburb of Barnsley to

the north, Cockle Creek and the Central-Coast Newcastle main passenger and freight train line to the east, Teralba and

Wakefield to the south and Killingworth to the west. The M1 Pacific Motorway and Sugarloaf State Conservation Area

adjoin the western boundary of the Site.

Teralba Southgate is located at 91 York Street, Teralba, approximately 1.5 km southeast of the Precinct, 400 m from

Teralba Train Station and 250 m from Booragul Train Station.

Strategic road and rail connections position the Site to support established and emerging industries and contribute to

a diverse post-mining economy. The Site also provides opportunities to protect and enhance natural systems, cultural

and historic assets, and support long-term community and environmental benefit.

The Site is located in a region with a strong and transferable skills base in mining, heavy industry, logistics,

construction and land management. As regional mining operations transition toward closure, these skills represent a

significant asset that can be redirected to support new and emerging industries.

The Master Plan identifies the arrangement of developable areas, environmentally constrained areas, recreational

areas, movement networks and key constraints across the Site and outlines the spatial logic for future development at

a precinct scale, providing a framework within which detailed design, subdivision and development assessment will

occur.

The Site is a non-operational mining site located within the Lake Macquarie Local Government Area (LGA) undergoing

rehabilitation. The Site forms part of a broader regional landscape that is undergoing economic, environmental and

land use transition as coal related activity declines and mining and energy assets are considered for alternative

productive land uses.

The Site has historically supported mining related activity and associated infrastructure. The Site now presents an

opportunity to consider future post-mining land uses that can deliver economic, social and community benefit while

responding to rehabilitation, environmental, infrastructure and planning requirements.

4 Cooperative Research Centre for Transformations in Mining Economies (CRC TiME) (2024) Inquiry into Beneficial and Productive Post-Mining Land

Use, Submission No. 67.

`

### Economics Report Page 13

`

3

This assessment tests how former mining land can be planned, enabled and transitioned to support employment-

generating land uses, regional economic resilience and broader community benefit.

Figure 1-1: Site context and Master Plan land use areas

Figure 1-1 shows the Site context and Master Plan land use areas, including developable areas, environmentally

constrained areas and further investigation areas.

1.2 Lake Macquarie's strategic role in regional transition economy

Lake Macquarie is strategically positioned within the Greater Newcastle and Hunter regional economy, with a large

employment base and strong connectivity to the Port of Newcastle, established freight networks, major transport

corridors, the Central Coast and Sydney. 5  These locational advantages support the area’s role in the Lower Hunter

economic system and provide a basis for future employment-generating land uses linked to regional transition.

The Lake Macquarie community strongly supports the economic transition away from coal alongside a clear

expectation that redevelopment delivers new jobs, affordable housing, and improved infrastructure.6 Residents place

high value on environmental quality, public spaces, and overall liveability, while expressing concerns about housing

affordability, transport connectivity, and involvement in decision-making.7

5 Lake Macquarie City Council (2024) North West Catalyst Area Place Strategy.

6 Lake Macquarie City Council (2025) Community Strategic Plan 2025–2035.

7Place Score (2023) 2023 Australian Liveability Census Lake Macquarie City Council - Priorities, Values and Performance Report

`

## 6. Traffic, Transport & Rail Infrastructure

### Traffic Report Page 3

`

Project number 531168-000  File Final_Traffic & Transport_Engineering Report Structure.docx  2026-07-13  Revision C

Executive summary

This Traffic and Transport Report has been prepared to support the State led rezoning and associated

master planning of the Macquarie Coal Complex (the Precinct) and Teralba South Gate sub-precinct

(collectively referred to as the Site), a large post mining landholding west of Cockle Creek in the Lake

Macquarie Local Government Area. The Site would be located between Teralba and Barnsley, framed by the

M1 Pacific Motorway to the west, the B89 George Booth Drive and Main Road corridor to the north and the

B53 arterial to the east. Wakefield Road is the key north-south spine through the area.

The Site would comprise approximately 211,100 m2 of large format warehousing across the Cockle Creek

and Killingworth employment cores, and a mixed-use core of around 18,100 m2 at West Lake. At full

development, the Site is anticipated to generate in the order of 12,470 daily trips of which 1,030 trips are

expected to be heavy vehicles and 300 RAV 19 metre B-doubles. Peak hour volumes are expected to be in

the order of 1,400 vehicles in the AM peak and 1,300 in the PM peak.

Midblock and intersection performance was reviewed across the base year and the short, medium and long

term, with and without the Precinct and a new Cockle Creek crossing. In the base year the network is

expected to operate at Level of Service (LoS) A to B, with only the Northville Drive corridor toward the B89

approaching LoS C to D.

Background growth is expected to drive the Northville Drive corridor to LoS E by the long term. The southern

and western network would remain at LoS A to C with the Precinct throughout. The Northville Drive and The

Weir Road intersections on the northern approach to the B89, would have adjoining links reaching LoS D in

the short term and level of service F by the long term and consequently have been identified for potential

upgrade, with proportionate contributions where they reach capacity under background growth.

Cockle Creek is a major line of severance for access in the wider area resulting in an already congested

network to the southeast of the precinct. Reducing future vehicle demands on existing creek crossings

through traffic management, mode shift, infrastructure upgrades and potential new infrastructure will be

appropriately incorporated within the onward planning for the precinct.

Three structural findings drive the network strategy:

◼ The approved RAV B-double network does not extend into the Precinct, and heavy vehicle access would

need to be newly established. Upgrading The Weir Road would provide the first compliant RAV route in

the short term, the Wakefield Road route to the M1 would follow in the medium term as the principal

freight route avoiding Barnsley, Holmesville and nearby schools. RAV access from the east through

Teralba could be considered in the long term but would likely require a new road and creek crossing to

bypass the grade constrained Rhondda Road

◼ Rhondda Road climbs features a sustained uphill climb of approximately 1 km for eastbound traffic with

grades ranging from 5 to 10%, followed by a sustained downhill descent of over 1 km at similar grades

with localised slopes over 12 per cent, beyond the Austroads limit for heavy vehicles, so the Precinct is

not accessible for freight from Teralba by the existing Rhondda Road alignment. Alternative eastern

access to the Precinct suitable for RAV would be a key part of the strategy, this could be a new Cockle

Creek crossing or upgrades to other infrastructure that currently restricts RAV access.

◼ The Five Islands Road crossing of Cockle Creek is the only principal crossing and already operates at or

near capacity. Therefore, the potential for a second crossing is a consideration in managing Precinct

traffic in the long term.

A staged upgrade program has been identified:

◼ Short term (0 to 10 years). Establish The Weir Road as a RAV 19 metre B-double route to the northern

access, deliver sub-precinct access intersections, and signalise and upgrade the Northville Drive

intersections at The Weir Road and the B89 as well as the Northville Drive / Appletree Road / Wakefield

Road intersection. Establish active transport links and extend public transport connections into the sub-

precincts

◼ Medium term (10 to 20 years). Upgrade and approve Wakefield Road as the principal RAV 19 metre B-

double route to the M1, upgrade the bridge over the railway in Teralba, deliver improved east-west

`

### Traffic Report Page 4

`

Project number 531168-000  File Final_Traffic & Transport_Engineering Report Structure.docx  2026-07-13  Revision C

connectivity via a new internal road connecting to Wakefield Road, and provide internal spine duplication

of the Northville Drive corridor.

◼ Long term (20 plus years). Protect and progress a direct M1 connection, potential reactivation of the

colliery rail loop with a south facing junction connecting to the Main North Rail Line, railway overpass over

Racecourse Road upgrade, and integration with the Lower Hunter Freight Corridor and High Speed Rail.

The assessment concludes that the proposed rezoning is not expected to be the sole contributor to future

constraints on the surrounding road network, with background growth of local traffic being a key driver of the

degradation in performance at the key intersections and corridors. Subject to the staged upgrade program

identified in this report, there are no presently known transport issues that would make the rezoning

inherently unfeasible.

`

### Traffic Report Page 5

`

Contents

Executive summary ........................................................................................................................................... i

1 Introduction .................................................................................................................................................. 1

1.1

Introduction ............................................................................................................................... 1

1.2

Purpose of this report ............................................................................................................... 1

1.3

Methodology ............................................................................................................................. 2

1.3.1

Baseline and Future horizons .................................................................................... 2

1.3.2

Existing trip patterns .................................................................................................. 2

1.3.3

Background traffic growth .......................................................................................... 2

1.3.4

Trip generation calculations ...................................................................................... 3

1.3.5

Trip distributions ........................................................................................................ 4

1.3.6

Road network performance ....................................................................................... 5

1.3.7

Traffic Assessment Assumptions .............................................................................. 8

1.4

Reliance on data and information ............................................................................................. 9

2 Strategic Context ....................................................................................................................................... 10

2.1

Regional Context and Connectivity ........................................................................................ 10

2.2

Federal ................................................................................................................................... 11

2.2.1

National Freight and Supply Chain Strategy ........................................................... 11

2.2.2

Sydney to Newcastle High Speed Rail .................................................................... 11

2.3

State ....................................................................................................................................... 11

2.3.1

Future Transport Strategy ....................................................................................... 11

2.3.2

NSW Movement and Place Framework .................................................................. 11

2.3.3

Hunter Regional Plan 2041 ..................................................................................... 11

2.3.4

Greater Newcastle Metropolitan Plan ...................................................................... 12

2.3.5

NSW Freight Policy Reform and the Lower Hunter Freight Corridor ...................... 12

2.3.6

Speers Point Transport Improvements (TfNSW) .................................................... 12

2.3.7

West Wallsend Rezoning ........................................................................................ 12

2.4

Local ....................................................................................................................................... 12

2.4.1

Lake Macquarie Local Strategic Planning Statement and Imagine Lake Mac

Community Strategy ................................................................................................ 12

2.4.2

Walking, Cycling and Better Streets Strategy ......................................................... 13

2.4.3

North West Lake Macquarie Catalyst Area Place Strategy..................................... 13

3 Baseline Analysis ...................................................................................................................................... 14

3.1

Road Network ......................................................................................................................... 17

3.1.1

State Roads ............................................................................................................. 19

3.1.2

Regional Roads ....................................................................................................... 20

3.1.3

Local Roads ............................................................................................................. 20

3.2

Crash statistics ....................................................................................................................... 21

3.3

Traffic Growth ......................................................................................................................... 23

3.4

Existing Trip Patterns ............................................................................................................. 24

3.5

Existing Midblock Performance Results ................................................................................. 24

3.6

Active Transport Network ....................................................................................................... 26

3.7

Bus Network ........................................................................................................................... 28

3.8

Rail Network ........................................................................................................................... 30

3.9

Freight Network ...................................................................................................................... 30

3.9.1

Road freight network ............................................................................................... 30

3.9.2

Rail freight network .................................................................................................. 30

3.10

Existing Traffic Issues ............................................................................................................. 33

3.10.1

Roundabout Congestion (Five Islands Road / The Esplanade / TC Frith Avenue) 33

`

### Traffic Report Page 7

`

Figure 3-7 Five Islands Road / The Esplanade / TC Frith Avenue Roundabout traffic conditions (Source:

ArcGIS Online Live Traffic Services, 9:30 am to 10:00 am)

Figure 3-8 William Street Bridge - Single Rail Crossing Point, Teralba

Figure 3-9 Rhondda Road Elevation Profile (Source: Google Earth)

Figure 4-1: Structure Plan (GHD, 2026)

Figure 4-2: Future road network - short term

Figure 4-3: Future road network - long term

Figure 4-4: Development scenarios - midblock assessment locations

Figure 4-5: Existing and future active transport network

Figure 4-6: Future heavy vehicle network - short term

Figure 4-7: Future heavy vehicle network – medium and long term

Figure 4-8: Road network upgrades by horizon

Figure 4-9: Indicative road cross sections (Lake Macquarie DCP 2014, Part 8 Subdivision Development,

Figure 12)

Tables

Table 1-1: Report structure

Table 1-2: Traffic generation rates (GTIA, 2024)

Table 1-3: Component rates adopted for the commercial mixed use and the resulting average (per 100 m2

GLA)

Table 1-4: Vehicle trip entry and exit distribution (GTIA, 2024)

Table 1-5: LoS traffic flow descriptions

Table 1-6: Level of Service description for road performance

Table 1-7: PCE factors per vehicle type (TfNSW Economic Parameter Values, 2025)

Table 3-1 Traffic and transport analysis summary

Table 3-2: Daily trip generation comparison against Badgerys Creek TMAP (2036)

Table 3-3: Crash degree definitions

Table 3-4: Reported crashes by severity, Precinct road network and surrounding corridors

Table 3-5: Most frequent crash types by Road User Movement (RUM) code

Table 3-6: Locations with the highest reported crash numbers

Table 3-7: Fatal crashes recorded along Precinct road network (2020-2024)

Table 3-8: 2026 baseline midblock performance

Table 3-9: Effect of grade on heavy vehicles (Austroads Guide to Road Design Part 3, Table 8.2)

Table 4-1: Indicative Precinct trip generation

Table 4-2: Indicative light vehicle distribution at full development

Table 4-3: Evidence basis for the adopted heavy vehicle market shares

Table 4-4: Indicative heavy vehicle origin and destination distribution (daily two-way trips)

Table 4-5: Light vehicle distribution summary by corridor (daily two-way trips)

Table 4-6: Heavy vehicle distribution summary by market (daily two-way trips)

Table 4-7: Short term - 2031 midblock performance

Table 4-8: Medium term - 2041 midblock performance

Table 4-9: Long term - 2041 midblock performance

Table 4-10: Indicative short term intersection performance

Table 4-11: Indicative medium term intersection performance

Table 4-12: Indicative long term intersection performance

Table 4-13: Summary of road network upgrades by horizon

Table 4-14: Road types and dimensions (Lake Macquarie DCP 2014, Part 8 Subdivision Development, Table

3)

Table 4-15: NSW roads and street principle (TfNSW Design of Roads and Streets (TS 00066:1.0), 2024))

Table 4-16: Movement and Place design parameters by street environment (TfNSW Design of Roads and

Streets (TS 00066:1.0), 2024))

`

### Traffic Report Page 8

`

Project number 531168-000  File Final_Traffic & Transport_Engineering Report Structure.docx  2026-07-13  Revision C

1

1

Introduction

1.1

Introduction

This Traffic and Transport Report (this Report) has been prepared by Aurecon on behalf of the Department

Planning, Housing and Infrastructure (DPHI) to support the State-led rezoning of the Macquarie Coal

Complex (the Precinct).  This Report assesses the proposed rezoning and accompanying Master Plan in

relation to traffic engineering and transport planning related matters.

This Report is structured as set out in Table 1-1.

Table 1-1: Report structure

Chapter

Description

Chapter 1 – Introduction

Explains the report's purpose and the methodology used to assess the rezoning. Covers

the baseline and future horizons, trip generation and distribution, network performance

approach, and data reliance.

Chapter 2 – Strategic

Context

Sets out the federal, state and local policy and planning framework the report responds

to. Includes freight, Movement and Place, regional plans and the local LEP, LSPS and

DCP.

Chapter 3 – Baseline

Analysis

Describes existing conditions across the road, active transport, bus, rail and freight

networks. Covers crash history, traffic growth, trip patterns, existing midblock

performance and the key existing traffic issues such as the Rhondda Road gradient and

severance features for future traffic connectivity such as Cockle Creek and the Main

Northern railway line.

Chapter 4 – Structure

Plan

Presents the proposed structure plan, transport network and traffic generation, then

assesses midblock and intersection performance across the horizons. Sets out the freight

and RAV route strategy, the integration of transport opportunities and the staged required

upgrades.

Chapter 5 – Conclusion

Summarises the baseline results against Precinct findings, a Cockle Creek crossing

benefit and the staged upgrade program. Concludes the rezoning is feasible subject to

staged delivery.

Appendices

Detailed midblock assessment results supporting the performance analysis.

1.2

Purpose of this report

This Report establishes an evidence based foundation to inform land use planning and infrastructure

decision making for the Precinct to support the rezoning. The Report has been prepared to:

◼ Support the development of the Master Plan including the establishment of the movement network

objectives, access arrangements and connectivity principles, and transport performance outcomes criteria

aligned with intended land uses.

◼ Inform State-led rezoning by demonstrating that proposed land use allocations are supported by feasible

and appropriate access arrangements, and that key transport opportunities and constraints are properly

integrated into land use planning and staging.

◼ Identify and prioritise transport infrastructure requirements necessary to enable development, including

key upgrades and new connections, and to establish indicative timing triggers across short, medium, and

long-term horizons (0-10, 10-20, and 20+ years respectively), supporting an orderly and coordinated

delivery of land use outcomes.

`

### Traffic Report Page 9

`

Project number 531168-000  File Final_Traffic & Transport_Engineering Report Structure.docx  2026-07-13  Revision C

2

1.3

Methodology

The assessment follows the TfNSW Guide to Transport Impact Assessment (GTIA) (TS00085 v1.1, 2024),

and the principles of the TfNSW Transport Management and Accessibility Plan, supported by the Austroads

Guide to Traffic Management (Parts 3 and 12) and the Austroads Guide to Road Design. The methodology

applied to each component of the assessment and is set out in the following sections.

1.3.1

Baseline and Future horizons

The baseline and future horizons adopted are as follows:

Horizon

Description

Base year (2026)

The existing network with current background traffic and no Precinct development. This

establishes the baseline against which each future horizon is compared.

Short term (+5 years)

Background traffic is grown to 2031 and the Precinct is partially developed. Full build

out is not expected within this horizon and a development reduction factor of

50 per cent is applied to the generated traffic.

The key road network connectivity links, being a new Cockle Creek crossing, the

railway overpass upgrade in Teralba and the proposed internal local road facilitating

east-west access to the site, are assumed not yet to developed, as well as the

formalisation of Wakefield Road, south of Rhondda Road as an approved RAV B-

double route. This results in site access to Area 1 being primarily from the northern and

southern access points via B89.

Medium term (+15 years)

Background traffic is further projected to 2041 and the Precinct is assumed to be at full

build out, with full generation applied (no reduction factor). The connectivity links,

including a new Cockle Creek crossing, the completion of upgrades to the railway

overpass, development of the internal east-west local road and approval of Wakefield

Road, south of Rhondda Road as a RAV B-double route, are assumed to have been

established, activating the eastern access point to the Precinct.

Long term (+20 years)

Full build out and the connectivity links in place, with background traffic further projected

to 2051.

1.3.2

Existing trip patterns

Existing travel behaviour is established from ABS Census data for 2016 and 2021. Vehicle ownership trends

are assessed at the Bolton Point to Teralba SA2 level by comparing the distribution of motor vehicles per

dwelling between the two census years and against the NSW average, indicating the degree of car

dependency that new land uses must plan around.

Journey to work (JTW) patterns are assessed from ABS 2021 Census data tabulating place of usual residence

by place of work at the SA2 level, for the suburbs in and around the master plan area (Teralba, West Wallsend,

Barnsley, Holmesville, Edgeworth, Fassifern and Wakefield), identifying the dominant modes, the share of

public and active transport and the principal origin and destination markets. These patterns inform both the

mode share assumptions and the geographic distribution of light vehicle trips.

1.3.3

Background traffic growth

Background traffic data was drawn from several sources, each covering a different part of the network and

period. The sources are as follows:

◼ Draft West Wallsend Rezoning TIA (GHD, 2025), providing 2024 survey volumes at a number of key

intersections and the STFM (TZP22STMV3.93) growth rates.

◼ TfNSW permanent classifier stations on the corridors surrounding the study area. Annual Average Daily

Traffic (AADT) is compiled for each station over the available data periods providing a long‑term dataset

suitable for understanding historic traffic patterns. with the 2020 and 2021 COVID-19 affected years

`

### Traffic Report Page 14

`

Project number 531168-000  File Final_Traffic & Transport_Engineering Report Structure.docx  2026-07-13  Revision C

7

LOS

Arterial

Sub-arterial

Collector

Local

VCR

Capacity

VCR

Capacity

VCR

Capacity

VCR

Capacity

E

1.00

1,400

1.00

1,200

1.00

1,000

1.00

900

F

>1

>1

>1

>1

Passenger car equivalent

For the purpose of the midblock assessment, all vehicles travelling in each direction were also converted to

the Passenger Car Unit (PCU). As per TfNSW’s recommended use of the Passenger Car Equivalent (PCE)

table from Transport for NSW Economic Parameter Values (2025), passenger and light vehicles are

considered as 1.0 PCU. Heavy vehicles are converted to passenger car units using a PCE of 8 for  general

B-double volumes, and 3.0 for general access heavy vehicles. The PCE factors per vehicle type are

provided in Table 1-7.

Table 1-7: PCE factors per vehicle type (TfNSW Economic Parameter Values, 2025)

Vehicle type

PCE factors

Passenger vehicles & LCVs

1.00

Rigid trucks

3.00

Trailers

6.00

Articulated trucks

5.00

B-doubles

8.00

Double road trains

8.00

Triple road train

10.00

2 axle buses

2.00

3 axle buses

3.00

Intersection performance

Intersection modelling was not undertaken for this assessment as base traffic volumes and performance was

not available, therefore only qualitative assessment was undertaken. For the qualitative assessment,

approaching midblock LoS were adopted as a guide to suggest intersection performance, as follows:

◼ Intersections between midblock segments with reserve capacity (LoS C or better) would generally

operate with reasonable levels of services

◼ Intersections with any adjoining approach midblock capacity of LoS D or above may be subject to poorer

LoS D and therefore may require upgrades

`

### Traffic Report Page 16

`

Project number 531168-000  File Final_Traffic & Transport_Engineering Report Structure.docx  2026-07-13  Revision C

9

1.4

Reliance on data and information

Advice and recommendations in this report rely on the accuracy of the existing input documentation and

advice provided to date, including:

◼ Post Mining Land Use – Deliverability of Pilot Projects – Due Diligence Report – Macquarie Coal Complex

(Aurecon, February 2026)

◼ Preliminary statutory planning due diligence (Patch Planning)

◼ Draft West Wallsend Rezoning Traffic and Transport Assessment (GHD, August 2025)

◼ West Wallsend Colliery, Killingworth Continued Operations Project – Traffic Impact Assessment

(Stapleton Transportation & Planning Pty Ltd, 2010)

◼ Teralba Sustainable Resource Centre Traffic Assessment (AECOM, 2010)

◼ Insights from internal workshops with DPHI, specialists and agencies

◼ Updated traffic surveys have not been undertaken for this assessment. Survey data has been adopted

from the West Wallsend assessment (November 2024 counts) and is to be refreshed before exhibition.

`

## 7. Flooding & Water Management

### Flooding Report Page 3

`

Project number 531168-000  File Final Flooding & WCM Engineering Report_CLEAN.docx  2026-07-01  Revision B

Executive summary

This Flooding and Water Cycle Management Report (This Report) presents a strategic flooding and water

cycle management (WCM) assessment for the Macquarie Coal Complex Precinct (the Precinct) and Teralba

Southgate to support a state-led rezoning and Master Plan. The assessment confirms that the Precinct can

be developed with a coordinated flooding and water cycle management strategy that supports future land

use while protecting people, property, infrastructure and the surrounding environment.

The assessment has been undertaken at a master planning scale using available flood studies, water cycle

data, site investigations and topographic analysis. It focuses on identifying key constraints, opportunities and

system behaviours rather than detailed design. On this basis, it demonstrates that flooding, stormwater,

water quality and emergency management outcomes are practically achievable across the Precinct through

an integrated, precinct-scale approach.

Flooding Strategy and Precinct Response

Flooding is a defining characteristic of the Precinct, driven predominantly by regional flooding from Cockle

Creek, supported by local overland flow processes and downstream tidal influences. These mechanisms

establish the spatial framework for development by identifying where land should be protected, where

development can occur, and where mitigation is required.

The Master Plan adopts a fundamental strategy of avoidance first, followed by selective, managed

encroachment in lower impact areas where development can be supported without increasing risk. This

approach preserves key floodplain functions while maximising viable development land.

The recommended flooding strategy is based on several core principles:

 Preservation of primary floodways and conveyance corridors

 Retention of flood storage areas and natural drainage pathways

 Direction of development toward areas of lower flood risk

 Integration of flood mitigation measures to support safe development

This approach ensures that development responds to the floodplain rather than working against it,

maintaining the hydraulic integrity of the system while enabling growth.

Protection of Surrounding Environment and Property

A key outcome of the assessment is that the proposed strategy protects both the environmental values of the

Precinct and the surrounding catchment, while avoiding adverse impacts on adjacent landholdings.

The Precinct drains to sensitive receiving environments including Cockle Creek, Burkes Creek, Diega Creek

and Lake Macquarie, which contain important ecological features such as riparian corridors, wetlands and

key fish habitat.

The master plan integrates these systems into the development framework by:

 Maintaining riparian corridors as functional flood conveyance and ecological buffers

 Protecting water quality through integrated treatment and management measures

 Avoiding increases in downstream flood risk or changes to flow behaviour

 Ensuring no material transfer of flood or drainage impacts to neighbouring land

This ensures that future development does not degrade environmental value or increase risk beyond the

site, a critical requirement for strategic planning and approval.

`

### Flooding Report Page 4

`

Project number 531168-000  File Final Flooding & WCM Engineering Report_CLEAN.docx  2026-07-01  Revision B

Deliverability of Mitigation Within the Precinct

A significant finding of the assessment is that the majority of required mitigation measures can be

accommodated within the Precinct footprint. This includes:

 Floodway corridors and overland flow paths

 Regional and local detention systems

 Stormwater conveyance networks

 Water quality treatment infrastructure

 Landform adjustments to manage flow and storage

These measures can be embedded into the structure of future development, allowing flood risk and water

cycle objectives to be addressed without reliance on extensive off-site works or unacceptable external

impacts.

This outcome demonstrates that the Precinct is not constrained in a way that precludes development, but

instead requires a coordinated and integrated design response at the master planning level.

Master Plan Intent and Flexibility

The master plan establishes a clear, achievable and flexible framework for future development. It defines the

spatial logic, performance objectives and key principles required to guide design and approvals, rather than

prescribing a single fixed engineering solution.

Importantly:

 The strategy is intended to be implemented progressively

 Future proponents can refine and adapt solutions

 Any modifications must remain consistent with the overall objectives

 All outcomes must comply with relevant legislation, policy and performance criteria

This ensures the plan remains practical and adaptable to future land use changes, evolving design

approaches and updated technical standards, while maintaining a consistent approach to flood risk and

water management.

Demonstrated Feasibility at Strategic Level

Based on the site review and strategic assessment, all key aspects of flooding and water cycle management

are considered feasible across the Precinct.

This includes:

 Flood risk management and land use compatibility

 Stormwater collection, conveyance and discharge

 Water quality management and protection of receiving environments

 Emergency access and evacuation planning

While further modelling and design will be required at later stages, the assessment confirms that there is a

credible and workable pathway to achieve these outcomes within future development.

Future Opportunities and Sustainable Water Strategies

In addition to conventional infrastructure, the Precinct presents opportunities to adopt more sustainable and

integrated water cycle approaches that reduce reliance on traditional systems.

`

### Flooding Report Page 5

`

Project number 531168-000  File Final Flooding & WCM Engineering Report_CLEAN.docx  2026-07-01  Revision B

Potential strategies include:

 Stormwater harvesting for non-potable reuse at lot or precinct scale

 Rainwater capture systems to reduce runoff volumes

 Passive irrigation of landscapes and green infrastructure such as through the use of street trees

 Distributed bioretention, detention and infiltration, where ground conditions allow

 Integration of water sensitive urban design (WSUD) across the development

These strategies can:

 Reduce demand on downstream drainage infrastructure

 Improve water quality outcomes

 Enhance resilience to climate variability

 Support more efficient and sustainable long-term servicing

Collectively, they represent a pathway toward a lower impact, more adaptive water management system for

the Precinct.

Conclusion

Overall, the flooding and water cycle management assessment supports a master plan that is practical,

flexible and environmentally responsible. It demonstrates that development within the Precinct can proceed,

provided that key floodplain functions are maintained and an integrated strategy is implemented.

The proposed approach protects surrounding communities and environmental systems, accommodates

required mitigation within the site, and establishes a robust framework to guide future planning, design and

delivery.

`

### Flooding Report Page 6

`

Contents

Executive summary ........................................................................................................................................... i

1 Introduction .................................................................................................................................................. 1

1.1

Site location and context .......................................................................................................... 2

1.2

Purpose of this Report .............................................................................................................. 4

1.3

Scope ....................................................................................................................................... 4

2 Information Sources, Assumptions and Limitations ............................................................................... 5

2.1

Data Sources Reviewed ........................................................................................................... 5

2.1.1

Documents and Local Study Review ......................................................................... 5

2.1.2

Data Collection .......................................................................................................... 6

2.2

Assumptions, Limitations and Dependencies .......................................................................... 6

3 Site and Water Context ............................................................................................................................... 8

3.1

Relevant Legislations, Policy and Guidelines .......................................................................... 8

3.1.1

Water Quality Policy and Guidelines ....................................................................... 12

3.1.2

Council Onsite Detention Requirements ................................................................. 19

3.1.3

Controlled Activities on Waterfront Land ................................................................. 19

3.2

Catchment, Waterways and Receiving Environments ........................................................... 21

3.2.1

Climate and Rainfall ................................................................................................ 21

3.2.2

Catchment and local topography ............................................................................. 23

3.2.3

Watercourses .......................................................................................................... 24

3.2.4

Tidal Limits .............................................................................................................. 26

3.2.5

Soils ......................................................................................................................... 27

3.2.6

Groundwater ............................................................................................................ 29

3.2.7

Existing Land Zoning ............................................................................................... 30

3.2.8

Sensitive Receiving Environments .......................................................................... 31

3.2.9

Preliminary Riparian Corridor Extent ....................................................................... 34

3.2.10

Indigenous Values of Lake Macquarie .................................................................... 35

3.3

Existing Drainage and Water Management Infrastructure ..................................................... 35

3.4

Mine Rehabilitation and Post-Mining Water Context .............................................................. 37

4 Existing Flood Risk ................................................................................................................................... 37

4.1

Flood Mechanisms and Flood Behaviour ............................................................................... 38

4.1.1

Regional Flooding .................................................................................................... 38

4.1.2

Local Flooding ......................................................................................................... 39

4.1.3

Tidal Inundation ....................................................................................................... 40

4.2

Hydraulic Categorisation (Flood Function) ............................................................................. 41

4.3

Flood Hazard, Life Safety and Land Use Compatibility .......................................................... 42

4.3.1

Flood Hazard and Life Safety .................................................................................. 42

4.3.2

Land Use Compatibility ........................................................................................... 42

4.4

Extreme Event Risk ................................................................................................................ 43

4.4.1

Probable Maximum Flood (PMF) Risk .................................................................... 43

4.4.2

Dam Failure Risk ..................................................................................................... 44

4.5

Emergency Management ....................................................................................................... 45

4.5.1

Emergency Management Strategy .......................................................................... 45

4.5.2

Flood Emergency Response Classification ............................................................. 46

4.5.3

Flood Sensitive Transport Links .............................................................................. 48

5 Drainage Feasibility and Existing Constraints ....................................................................................... 49

5.1

Drainage Constraints and Development Implications ............................................................ 49

`

### Flooding Report Page 7

`

5.2

Overland Flow Paths and Outlet Points ................................................................................. 50

5.3

Groundwater, ASS and Salinity Considerations ..................................................................... 51

6 Water Cycle Management Assessment .................................................................................................. 53

6.1

Integrated Water Cycle Management Pathway ...................................................................... 53

6.2

Water Cycle Management Opportunities ............................................................................... 53

6.2.1

Existing Infrastructure .............................................................................................. 53

6.2.2

Harvesting and Reuse ............................................................................................. 54

6.2.3

Treatment ................................................................................................................ 54

6.2.4

Groundwater ............................................................................................................ 54

7 Structure Plan ............................................................................................................................................ 55

7.1

Proposed Structure Plan ........................................................................................................ 55

8 Flooding and Water Cycle Management Strategy .................................................................................... 3

8.1

Flood Management Strategy .................................................................................................... 3

8.1.1

Regional Detention Basins ........................................................................................ 3

8.1.2

Floodway Corridors ................................................................................................... 3

8.1.3

Bulk Filling and Flood Storage Offsets ...................................................................... 4

8.1.4

Non-Structural Management Measures .................................................................... 4

8.2

Stormwater Management Strategy ........................................................................................... 5

8.2.1

Stormwater Detention ................................................................................................ 5

8.2.2

Stormwater Conveyance ........................................................................................... 6

8.2.3

Natural Water Systems ............................................................................................. 7

8.3

Water Quality Management Strategy ....................................................................................... 7

8.3.1

Water Quality Targets ................................................................................................ 7

8.3.2

Water Sensitive Urban Design Treatment Train ....................................................... 9

8.3.3

On-lot Treatment ..................................................................................................... 10

8.3.4

Road Treatment ....................................................................................................... 10

8.3.5

End of Pipe Treatment ............................................................................................ 11

9 Integrated Spatial Planning Implications ................................................................................................ 12

9.1

Flooding Constraint Classification Framework ....................................................................... 12

9.1.1

High Flood Constraint Areas ................................................................................... 13

9.1.2

Moderate Flood Constraint Areas (Further Investigation Areas) ............................ 14

9.1.3

Lower Constraint Areas ........................................................................................... 14

9.1.4

Master Plan Implications ......................................................................................... 14

9.2

Integrated Water Management Strategy ................................................................................ 15

9.2.1

Impervious Assumption ........................................................................................... 15

9.2.2

Proposed Strategy ................................................................................................... 16

9.3

Interface With Other Disciplines ............................................................................................. 18

10 Master Plan Objectives and Performance Criteria ................................................................................. 19

10.1

Proposed Objectives .............................................................................................................. 19

10.2

Proposed Performance Criteria .............................................................................................. 19

11 Staging Triggers and Later-Stage Investigations .................................................................................. 20

11.1

Triggers Table ........................................................................................................................ 20

11.2

Exclusions and Deferred Items .............................................................................................. 22

12 Conclusions and Recommendations ...................................................................................................... 23

12.1

Summary of Findings.............................................................................................................. 23

12.2

Recommendations for the Master Plan .................................................................................. 24

`

### Flooding Report Page 8

`

13 References ................................................................................................................................................. 25

Figures

Figure 1-1 Regional context and connectivity from GHD Macquarie Coal Complex Pilot Project Master Plan

2026

Figure 3-1 Risk of impact to Lake Macquarie Estuary

Figure 3-2 NSW Water Quality Objectives – Lake Macquarie and Tuggerah Lakes

Figure 3-3 NSW Water Quality Objective Zones for Precinct (indicative location marked in red)

Figure 3-4 Strahler order system (DPE, 2022a)

Figure 3-5 Riparian corridor (DPE, 2022b)

Figure 3-6 Evaporation and rainfall climate data

Figure 3-7 Average monthly maximum and minimum temperature data

Figure 3-8: Catchment and topography

Figure 3-9 Slope of site

Figure 3-10 Tidal Limits

Figure 3-11 Geomorphology, river condition and soils

Figure 3-12 Soil landscapes

Figure 3-13 Available ground investigation locations

Figure 3-14 Existing land zoning

Figure 3-15 Groundwater dependant ecosystems

Figure 3-16 Sensitive receiving environments

Figure 3-17 Preliminary vegetated riparian zone

Figure 3-18 Existing water management infrastructure

Figure 4-1 PMF and 1% AEP Flood extents map

Figure 4-2 Local overland flow paths

Figure 4-3 Coastal hazards

Figure 4-4: Land use compatibility in flood prone areas

Figure 4-5: Dam failure inundation area with PMF flood hazard

Figure 4-6 Flood emergency response classification map of the development area

Figure 5-1: Indicative Drainage Constraints

Figure 5-2: Indicative Existing Overland Flow Paths

Figure 7-1 Structure plan

Figure 7-2 Structure Plan with sub-precincts

Figure 8-1: Typical floodway corridor example

Figure 8-2: Conceptual Floodplain Filling and Flood Storage Offset Arrangement

Figure 8-3 Percentage impervious surfaces of each sub-precinct and 1% AEP flood extent.

Figure 8-4 Developable areas requiring NorBE

Figure 8-5 Indicative WSUD treatment train proposed for the Precinct

Figure 8-7 Example of bioretention street tree (Blacktown City Council, 2026)

Figure 9-1 Land Use Compatibility Constraints

Figure 9-2 Land Use Compatibility Constraints – Master Plan overlay

Tables

Table 2-1 Documents, Developments and Local Study Review

Table 2-2 Summary of the data supplied for review

Table 2-3: Summary of assumptions, limitations and dependencies

Table 3-1 Relevant legislation

Table 3-2 Relevant policies and guidelines

Table 3-3 Nutrient loading limits for Lake Macquarie Estuary

Table 3-4 Lake Macquarie City Council DCP stormwater management targets

`

### Flooding Report Page 9

`

Table 3-5 Water quality objectives for the Lake Macquarie and Tuggerah Lakes catchment

Table 3-6 Riparian corridor widths (DPE, 2022b)

Table 3-7 Riparian corridor matrix (DPE, 2022b)

Table 3-8 Rainfall and evaporation data statistics

Table 3-9 Summary of water quality for Council data

Table 3-10 Summary of water quality data from Glencore monitoring

Table 3-11 Tidal planes for Lake Macquarie at Marmong Point (211460) (MHL 2025)

Table 3-12 Soil landscapes of the Precinct

Table 3-13 Groundwater wells summary (WaterNSW, 2025)

Table 3-14 Groundwater Dependent Ecosystems in Precinct

Table 5-1 Drainage implications based on slope constraints

Table 6-1 Examples of treatment trains and scales

Table 7-1 Land Use Analysis

Table 8-1 Developable area

Table 8-2 Preliminary pre-development pollutant loads for 1hectare greenfield areas based on two example

soil types

Table 8-3 WSUD Measures proposed

Table 9-1: Constraint and developability levels

Table 9-2 Impervious % from DCP

Table 9-3 Impervious % based on land use

Table 9-4 Integrated Water Management Strategy for each sub- precinct

Table 11-1 Trigger framework

`

### Flooding Report Page 11

`

Project number 531168-000  File Flood & WCM Report  2026-07-01  Revision B           1

1

Introduction

This report confirms that the Precinct can be planned with a practical and achievable flooding and water cycle

management strategy that supports future development while protecting people, property, infrastructure and the

surrounding environment. The assessment has been undertaken at a strategic master planning level and is based

on a review of the site, available flood studies, water cycle management information, topography, waterways,

receiving environments and existing infrastructure. On that basis, the overall conclusion is that the key flooding,

stormwater, water quality and evacuation outcomes for the Precinct are capable of being achieved through a

coordinated precinct-scale approach, subject to detailed design in later phases.

Flooding is a defining consideration for the Precinct, particularly in relation to Cockle Creek, its tributaries, local

overland flow paths and downstream tailwater influences. However, the report demonstrates that these constraints

do not preclude future land use planning. Rather, they establish a clear framework for where development should

occur, where flood conveyance and storage should be maintained, and where supporting mitigation is required.

The proposed flooding strategy is built around preserving key floodways, accommodating regional flow paths,

providing detention and storage where necessary, and locating future development in areas that can achieve an

acceptable level of flood risk management. This creates a structure for growth that responds to the floodplain rather

than working against it.

A key message of the assessment is that the proposed strategy protects the environmental values of the site and

the surrounding catchment, while also avoiding the transfer of flood impacts to neighbouring landholdings. The

Precinct contains and drains to sensitive receiving environments, including Cockle Creek, Burkes Creek, Diega

Creek and Lake Macquarie. It also contains riparian corridors, wetlands, key fish habitat and other ecological

values that require protection. The recommended approach maintains these systems as important components of

the masterplan, allowing them to continue functioning as flood conveyance corridors, ecological buffers and water

quality protection features. In this way, the strategy is not only about making development possible, but about

ensuring that the surrounding environment and adjoining properties remain protected from increased flood risk,

water quality decline or inappropriate drainage outcomes.

Importantly, the report finds that many of the mitigation measures needed to support future development can be

accommodated within the Precinct footprint. This includes the retention of floodway corridors, provision of regional

or local detention, integration of stormwater conveyance pathways, on-site detention, water quality treatment

systems and landform responses that work with the site’s natural drainage patterns. While detailed sizing and

alignment of infrastructure will need to be resolved by future proponents, the strategic assessment demonstrates

that sufficient opportunities exist within the Precinct to embed these measures into future development layouts.

This is a significant outcome because it shows that the masterplan can establish a viable pathway forward without

relying on unreasonable off-site intervention or unacceptable impacts to external land.

The intent of the masterplan is therefore to set an achievable and defensible strategy at a precinct scale, rather

than prescribe a single fixed engineering outcome. The report makes clear that future proponents may modify

elements of the ultimate flooding and water cycle response as individual development proposals evolve, provided

the overall objectives of the masterplan are maintained and all relevant legislation, policy and performance criteria

are met. This is an important distinction. The report does not seek to lock in detailed design at rezoning stage.

Instead, it establishes the spatial logic, technical principles and performance expectations needed to guide future

planning, design and approvals in a consistent way.

Based on the site review and high-level strategic assessment completed for this report, all core aspects of

stormwater management, flooding response, water quality management and emergency evacuation are considered

practically achievable across the Precinct. This does not remove the need for future modelling, detailed design,

staging reviews and approval pathways. However, it does confirm that there is a credible and workable route to

resolving these matters through later project phases. In particular, the report shows that flood-compatible land use

planning, structured drainage networks, protection of overland flow paths, water quality treatment trains and future

emergency access planning can all be integrated into the development of the Precinct in a practical manner.

Looking ahead, there is also an opportunity to reduce demand on conventional water cycle management

infrastructure by exploring more sustainable and integrated servicing strategies as the Precinct develops. These

`

### Page 11

Precinct constraints

The Precinct presents a range of environmental, physical and infrastructure

constraints that are managed through the structure plan and addressed

progressively through staged development and site-specific assessment at the

development application stage.

Geotechnical stability and risk management – Development on the TSF and the

land located in the dam break inundation zone to the north is currently limited.

Soft alluvial soils located around the coastal wetlands in the north of the site

influence construction methods.

Environmental – Existing areas of high biodiversity values, high bush fire risk

and flood affected areas require further investigation to inform development

siting and design.

Sensitive uses – Interfaces between existing land uses, including residential

receivers and potential future industrial land uses will need to be managed to

mitigate negative noise, odour and visual impacts.

Infrastructure – Heavy vehicle access to parts of the site is currently limited

due to steep gradients, access through local residential areas and existing rail

crossings. The location of the existing oil pipeline, electrical transmission lines

and their associated easements, setbacks and design measures will need to be

considered.

Utility infrastructure – Viability and sequencing of the provision of utilities,

particularly to the West Lake sub-precinct, will need further investigation.

11

2  Strategic context

-

### Page 12

Precinct vision

3	 Macquarie Coal

Complex Precinct

Figure 6: Vision: A new generational-scale employment precinct for the Hunter

12

### Page 13

Economic diversification and employment

•

A generational-scale opportunity to transform

former mining land into the Lower Hunter’s

premier employment precinct, delivering diverse

jobs and well-located employment land at a

regionally significant scale.

•

Enable a diversity of employment-generating

land uses that support regional economic

diversification, attract investment and create

local jobs.

•

A master planned, single-ownership Precinct

that attracts investment through flexible lot

configurations, co-location of complementary

industries and accommodation of large-footprint

uses.

•

A flexible, staged delivery framework that

aligns with mine closure commitments,

infrastructure capacity and changing economic,

social and market conditions, for the orderly

transformation from rehabilitation to productive

post mining uses.

Infrastructure and mobility

•

Leveraging existing transport connections to

deliver an efficient, well-serviced employment

precinct, with a legible internal road hierarchy

that supports safe and equitable access for

freight, workforce, public transport and active

transport users.

•

Utilities and services that meet the current

and future servicing needs of the Precinct,

whilst minimising land impacts and maximising

reliability, efficiency and sustainability.

Guiding principles

The guiding principles establish the Precinct-wide directions for land use, infrastructure, environmental

management, design quality and community benefit. They are to guide future planning, development

assessment, addenda to the draft Master Plan and staged implementation.

13

3  Macquarie Coal Complex Precinct

### Page 14

Environment and resilience

•

A connected network of high-value biodiversity,

wetlands and riparian corridors retained as

integral elements of the Precinct.

•

Encourage restorative and resilient development

that responds to biodiversity values, flood-prone

areas, drainage systems and minimises

cumulative impact.

•

Land use and development enable a coordinated

transformation to net-zero emissions.

•

A precinct-scale approach to managing post

mining constraints through a staged, risk-

informed framework that progressively develops

land as conditions mature.

•

Support circular economy models through

the co-location of complementary industries that

can share resources, infrastructure

and services, reducing waste and improving

resource efficiency.

Place and community benefits

•

A distinctive post mining landscape identity,

where rehabilitating landforms, remnant native

bushland, waterways and ecological corridors

shape the Precinct’s character and sense of

place.

•

High-quality urban design and public realm

outcomes with built form, subdivision

and interface treatments that respond to

topography, rehabilitated landforms and the

broader environmental and cultural setting.

•

Integrated community-supporting facilities co-

located with employment areas and public open

space, delivering tangible community and public

benefit at a scale that complements the

Precinct’s primary employment function.

•

Leveraging West Lake and environmentally

constrained areas to provide accessible

recreation, nature-based tourism and connected

trail and active transport network for workers,

surrounding communities and visitors.

14

3  Macquarie Coal Complex Precinct

### Page 15

mining land uses. It establishes the foundation for

planning, design and development to be guided by

the principles of the Government Architect NSW

Connecting with Country Framework.

As the draft Master Plan is exhibited and refined,

meaningful engagement with Lake Macquarie

Aboriginal community stakeholders will form

an important part of the process to refine and

finalise the draft Master Plan. This should include

engagement with Traditional Custodians, Aboriginal

knowledge holders, the Awabakal Local Aboriginal

Land Council, the Biraban Local Aboriginal Land

Council and other Aboriginal organisations or

representatives identified through the engagement

process.

Connecting with Country

The Precinct is located on Awabakal Country,

adjacent to the shores of Cockle Bay in the north

of Lake Macquarie. The draft Master Plan

recognises Country as a living system of

interconnected cultural, ecological and physical

relationships, including land, waters, skies, plants,

animals, cultural practices, stories and community.

It also recognises that planning for the

transformation of a former mining landscape must

be informed by an understanding of Country and

respectful engagement with Aboriginal people

who hold cultural knowledge, rights and

responsibilities for the area.

The draft Master Plan has been prepared as an

early framework for the transformation of the

Precinct from mining to sustainable and

productive post

Credit: Glencore

15

3  Macquarie Coal Complex Precinct

### Page 16

Structure plan

The structure plan (Figure 9) is the principal

spatial framework for the draft Master Plan. It

identifies the arrangement of developable areas,

environmentally constrained areas, recreational

areas, movement networks and key constraints

across the Precinct to guide development.

The structure plan outlines the spatial logic for

future development at a precinct scale, providing

a framework within which detailed design,

subdivision and development assessment will

occur. The structure plan is supported by technical

studies.

The following categories are used to describe land

within the structure plan:

•

Developable areas – Land that is potentially

suitable for development, subject to further

technical investigation and site-specific

assessment at the development application

stage.

•

Environmentally constrained areas – Land

identified as having biodiversity values or where

natural features (watercourses, wetlands, steep

slope, flooding) constrain development.

•

Recreation areas – Land potentially suitable for

active and passive recreation facilities,

balanced with protecting biodiversity and

cultural values.

•

Further investigation – Potentially developable

land that is constrained in the short to medium

term by geotechnical, dam safety, biodiversity

or flood risk factors, requiring resolution before

development can proceed. Development of this

land is contingent upon the completion

of relevant technical investigations and the

achievement of applicable staging triggers.

4	 Structure plan and

sub-precinct framework

Figure 7: Indicative visualisation east over

Macquarie Coal Complex Precinct

Figure 8: Indicative visualisation west over

Macquarie Coal Complex Precinct

16

### Page 17

Figure 9: Macquarie Coal Complex Precinct Structure Plan

17

4  Structure plan and sub-precinct framework

### Page 18

Sub-precinct framework

The structure plan organises the Precinct into

five development sub-precincts (Figure 10), set

within a connected network of environmentally

constrained areas that define the Precinct’s

landscape framework. Each sub-precinct presents

a distinctive opportunity, shaped by its topography,

legacy mining features, environmental values,

access and proximity to existing communities and

infrastructure.

Together the sub-precincts enable a coordinated,

staged transformation of the Precinct that

responds to physical setting while delivering

a diverse range of employment, recreation

and community outcomes. Each sub-precinct

description presents key characteristics, land use

intent and opportunities for future planning and

development, against which development proposals

will be assessed.

Figure 10: Sub-precincts

18

4  Structure plan and sub-precinct framework

### Page 19

Land use intent

Future development will be anchored by

employment-generating activity that supports

regional economic diversification, attracts

investment and creates local jobs. Complementary

commercial, recreation, community and visitor land

uses will support the workforce, deliver community

benefit and contribute to the broader public value

of the post mining tranformation.

Figure 11: Employment land use envisaged in the Precinct

Figure 12: Complementary land use typologies envisaged

19

4  Structure plan and sub-precinct framework

### Page 20

Cockle Creek

Characteristics

Cockle Creek sub-precinct is located in the eastern

portion of the Precinct and encompasses the

former MCPP, TSF, mine rail loop and associated

operational infrastructure. Its direct interface

with the Main Northern Railway, together with

established access from Racecourse Road,

Railway Street and The Weir Road, positions the

sub-precinct as a strategically connected gateway

within the broader Precinct.

Historic industrial use has shaped a substantially

modified landscape of previously disturbed land

and legacy infrastructure. These attributes provide

a strong foundation for early activation and support

the efficient reuse of land.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform a flexible,

opportunity-led planning response:

•

Reuse of legacy industrial assets – The former

coal preparation plant, mine rail loop and

existing rail interface with the Main Northern

railway provide a platform for new industrial,

manufacturing, energy and rail-related uses that

leverage available infrastructure.

•

Early activation of available land – Areas outside

the TSF and dam break inundation zone are well-

positioned for near-term development, with

further land progressively released as TSF

rehabilitation advances.

•

Enhanced connectivity – A potential new bridge

crossing of Cockle Creek is identified for

investigation to strengthen road access and

unlock additional development opportunities

across the sub-precinct.

•

Improved internal movement networks – New

internal road links will support integrated

movement across the sub-precinct, enabled by

revocation of the TSF dam declaration or

delivery of bridge infrastructure above the

inundation level.

•

Supporting industries that would facilitate rail

manufacturing, including workshops with skilled

trades.

•

Established access for short term activity

– Existing connections from Railway Street,

Racecourse Road, The Weir Road and Rhondda

Road provide immediate access to developable

land beyond the dam break inundation zone,

supporting early-stage uses.

•

Integration of environmental values – High value

biodiversity, fauna habitat and wetland areas to

north and east of the sub-precinct are retained

and integrated into the land use pattern,

supporting a considered balance between

development and environmental outcomes.

Figure 13: Indicative mixed industrial development

concept

Figure 14: Indicative mixed industrial

development concept utilising rail connectivity

20

4  Structure plan and sub-precinct framework

### Page 21

Killingworth

Characteristics

Killingworth sub-precinct is located in the north-

western portion of the Precinct, near established

residential areas of Killingworth and Barnsley.

Accessible topography, established road

connections via Wakefield Road and The Broadway,

and a direct interface with environmentally

constrained areas and biodiversity corridors to the

south and east define its place-based setting.

Its proximity to existing communities and the

prevalence of previously disturbed land from

former mining operations position the sub-precinct

as a strong candidate for early activation. These

attributes provide a practical platform for short-

term development opportunities, aligned with

rehabilitation outcomes and sequenced provision of

servicing.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-led

planning response:

•

Compatible community interface – Interface

with established residential areas of

Killingworth and Barnsley is managed through

appropriate buffers, setbacks and acoustic

treatments to make sure land use compatibility

and protect amenity.

•

Efficient access and movement – Accessible

topography and established connections

through Wakefield Road and The Broadway

enable efficient site access, with heavy vehicle

routing strategy that directs freight to approved

routes and reinforces the sub-precinct’s

logistics advantages.

•

Energy-enabled employment opportunity –

Proximity to the Transgrid substation positions

Killingworth to attract energy-intensive and

data-driven industries seeking reliable grid

access, supporting the Precinct’s role in the

Hunter’s energy and digital economy

transformation.

•

Local jobs – The sub-precinct’s location

adjoining established communities provides for

accessible local employment that supports

workforce participation and liveability across the

surrounding area.

•

Integration of environmental values – Interfaces

with environmentally constrained areas and

biodiversity corridors inform a considered land

use pattern that retains ecological connectivity

while enabling productive use of previously

disturbed land.

•

Evidence-based sequencing – Geotechnical,

water quality, utilities and access investigations

will inform the staged delivery of development.

Figure 15: Indicative light industrial development

concept

Figure 16: Indicative light industrial layout

development concept

21

4  Structure plan and sub-precinct framework

### Page 22

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-

led, planning response:

•

A landscape-led destination – West Lake will

evolve as the Precinct’s landscape, community

and visitor heart, where rehabilitated land, water

and bushland frame a curated employment,

tourism, recreation and interpretation concept

that supports economic diversification and long-

term adaptability.

•

Signature landscape setting and visitor

experience – The lake and distinctive landscape

identity that supports nature-based tourism,

recreation and visitor infrastructure, including

walking and cycling trails, lookouts, water-based

facilities and heritage interpretation.

•

Integrated landscape and environmental values

– Rehabilitation areas, habitat corridors and

interfaces with rural landscapes and

environmentally constrained areas inform a

considered land use pattern, with buffer zones

and edge treatments that protect surrounding

values and reinforce ecological connectivity

across the Precinct.

•

Evidence-based sequencing – Geotechnical,

water quality, utilities and access investigations

will inform the staged delivery of development.

West Lake

Characteristics

West Lake sub-precinct occupies the south-

western portion of the Precinct and encompasses

the former Westside void, now a

water-filled lake, together with the surrounding

rehabilitation areas. The sub-precinct’s distinctive

landscape identity is shaped by the interplay of

water, remnant bushland, rehabilitated landforms

and elevated topography, with expansive views

across the Precinct and towards Lake Macquarie.

The lake is a signature landscape asset that

anchors a unique sense of place. It provides

the foundation for nature-based experiences,

recreation and visitor infrastructure that enhance

the Precinct’s broader attractiveness as an

employment and lifestyle destination. The sub-

precinct enables an active waterfront approach

to commercial, tourism and recreation around the

foreshore, with development carefully integrated

to retain and showcase the area’s biodiversity and

landscape values.

Further investigation areas on the eastern side of

the lake offer additional opportunity for low-impact,

sensitive development that responds to the desired

future character of West Lake and complements its

biodiversity and landscape setting.

Figure 17: Indicative lakeside development concept

22

4  Structure plan and sub-precinct framework

### Page 23

Barnsley West

Characteristics

Barnsley West sub-precinct is in the north-western

portion of the Precinct, comprising separate parcels

of land associated with the former Wakefield

Colliery. Accessed via Wakefield Road and Charlton

Street, the sub-precinct sits within a distinctive

landscape setting shaped by its interface with

adjoining residential areas, environmentally

constrained lands and established transmission

infrastructure. High biodiversity land between

Barnsley West and the Killingworth sub-precinct

reinforces its discrete identity.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-

led, planning response:

•

Small-scale urban services and light industry

– The sub-precinct’s compact scale and

adjacency to residential areas provide for a

curated mix of small-scale urban services, light

industrial and complementary employment

uses that meet local needs while supporting the

Precinct’s broader economic diversification.

•

Amenity-led interface with Barnsley village –

The residential interface informs a high-quality

edge response, including built form transitions,

landscape buffers, acoustic treatments and

operational controls, that protect the amenity

and character of the existing community.

•

Coordinated infrastructure interface – Existing

transmission easements are integrated into

the land use pattern, informing layout, access

and development footprints that align with

infrastructure outcomes and unlock practical

development areas.

Figure 18: Indicative small unit industrial development concept

23

4  Structure plan and sub-precinct framework

### Page 24

Teralba

Characteristics

The Teralba sub-precinct is located approximately

two kilometres south-east of the main Precinct,

adjoining the established Teralba local centre. The

sub-precinct is defined by its direct proximity to

two rail stations, its interface with the heritage-

listed Teralba Conservation Area, and its integration

with the established residential and commercial

fabric of the Teralba village.

Together, these attributes position Teralba as the

Precinct’s mixed use sub-precinct, a compact,

well-serviced setting where new housing and

complementary uses can support the ongoing

vitality of the local centre and contribute to the

broader regional transformation envisaged by the

Master Plan.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-led

planning response:

•

Conveniently connected and serviced –

Positioned approximately 300 metres from

Booragul Station and 400 metres from Teralba

Station, the sub-precinct enables direct access

to the regional passenger rail network and

supports a walkable, low-car neighbourhood

model.

•

Reinforcement of the Teralba local centre –

Proximity to established retail, community and

commercial services provides the foundation

for residential and complementary uses that

strengthen the centre’s economic base, activate

the public realm and support day-to-day

amenity for residents and workers.

•

Heritage-informed place-making – The setting

of the Teralba Conservation Area and local

heritage items, including the Miner’s Cottages

and Teralba Public School, informs a considered

design response that respects established

character, scale and views, and integrates

heritage interpretation as a defining element of

local identity.

•

Landscape-led response to Cockle Creek – The

Cockle Creek corridor informs a considered

land use pattern that balances development

opportunity with waterway health, riparian

amenity and flood conveyance, delivering

a high-quality blue-green edge to the sub-

precinct.

•

Enhanced pedestrian and cycling connectivity

– New and upgraded active transport links

to Teralba Station and across the railway

strengthen the sub-precinct’s transit-oriented

potential and improve everyday connections

between the neighbourhood, the local centre

and surrounding communities.

•

Early activation potential – Progress in mine

closure and rehabilitation, together with

established servicing connections, proximity to

existing urban areas and direct public transport

access, positions the sub-precinct as a strong

candidate for early activation and near-term

delivery.

24

4  Structure plan and sub-precinct framework

### Page 25

Environmentally constrained areas

Characteristics

Environmentally constrained areas form an integral

and defining element of the Precinct’s structure,

comprising tracts of remnant native vegetation,

rehabilitation areas, riparian corridors, waterways

and ecological networks distributed across

the Precinct. Together, these areas establish a

connected environmental framework that supports

biodiversity, water cycle management, landscape

identity and Connecting with Country outcomes.

Environmentally constrained areas anchor the

structure plan in a high-quality landscape setting

and reinforce ecological connectivity across the

region. The intent of these lands is to protect and

enhance environmental, hydrological, cultural and

landscape values over the long-term, while

enabling sensitive land use where suitable.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-

led, planning response:

•

Anchoring the Precinct’s ecological framework

– High biodiversity areas, key fish habitat

and terrestrial corridors provide north–south and

east–west ecological connectivity across the

Precinct. Biodiversity corridors, coastal

wetlands, mapped waterways and areas subject

to Voluntary Conservation Agreements

informing a clear protection framework aligned

with statutory requirements.

•

Considered, evidence-based approach to

compatible use – Where supported by detailed

biodiversity assessment, low-impact, compatible

uses may be accommodated within these lands,

guided by the recognised hierarchy of avoid first,

minimise where avoidance is not practicable, and

offset residual impacts. This approach makes

sure that future use is sensitively located,

limited in scale, and consistent with the

retention and enhancement of biodiversity,

hydrological and landscape values.

•

Water cycle and landscape performance –

Riparian corridors along mapped waterways

provide for flood conveyance, stormwater

treatment and waterway health, contributing to

a resilient water cycle framework that supports

development outcomes elsewhere in the

Precinct.

•

Compatible low-impact recreation and visitor

experience – Walking trails, lookouts, nature-

based education and interpretation position the

environmentally constrained areas as part of a

layered land use framework that complements

community benefit and economic diversification

across the Precinct.

Figure 19: Indicative view of environmentally

constrained areas

Figure 20: Indicative trails within the environmentally

constrained areas

25

4  Structure plan and sub-precinct framework

### Page 26

Implementation and sequencing

Implementation

The implementation and delivery of the entire

Precinct vision is intended to be sequenced over

several decades, reflecting the need to manage

mine closure and rehabilitation responsibilities and

to allow the future land uses to evolve in alignment

with development uptake. Delivery of supporting

infrastructure is intended to be staged to correlate

with the development as it is implemented over

time.

Development sequencing provides for

infrastructure delivery that is proactive but demand

led and enables early activation while supporting

long-term, efficient and resilient precinct

development. Infrastructure delivery is to be

adaptive, demand driven and coordinated, ensuring

that development does not outpace enabling

infrastructure while maintaining flexibility for

market led uptake. Development is to be staged in

accordance with available infrastructure capacity,

with priority given to feasibility of connecting

with existing utilities and transport networks.

Infrastructure delivery should adopt an integrated

and coordinated approach across utilities and

transport to minimise disruption and duplication.

26

4  Structure plan and sub-precinct framework

### Page 27

Figure 21: Staging and key levers

27

4  Structure plan and sub-precinct framework

### Page 28

Development horizons

Development horizons are described in Table

Figure 22 illustrates the sequencing of

development within the Precinct, which reflects

the horizon within which land would commence

development, subject to the drivers and staging

triggers.

Table 1: Sub-precinct staging

Horizon

Timeframe

Key sub-precincts and drivers

Short-term

activation

0–5 years

Cockle Creek, Killingworth, West

Lake, Barnsley West, Teralba.

Medium-term

activation

5–15 years

Cockle Creek, Killingworth.

Long-term

activation

15+ years

Cockle Creek and Killingworth

residual land.

Figure 22: Sub-precinct staging

28

4  Structure plan and sub-precinct framework

### Page 29

Short-term activation

Areas identified as being capable of early release

for post mining land use development share

common characteristics, including land where

rehabilitation is at or near completion, existing

road access is available, servicing connections are

feasible and the risk profile is manageable without

requiring major investigations or infrastructure

upgrades.

Early phases are expected to leverage available

capacity within the Argenton Substation, existing

potable water connections and established regional

freight corridors, minimising the need for major

upfront augmentation. These areas also align with

transport accessibility and heavy vehicle routing

capability, supporting early industrial and logistics

uses.

These short-term activation areas provide the

opportunity to demonstrate viability of post mining

land use shift, generate investment confidence and

deliver tangible employment and community

outcomes.

Cockle Creek

Previously disturbed areas outside the TSF and

dam break inundation zone with existing access to

the regional road network. Early activation within

this sub-precinct could leverage the existing rail

loop with opportunities for related manufacturing

facilities.

This sub-precinct benefits from the strategic role

of freight and logistics in this area, leveraging

proximity to supporting flexible, freight-adjacent

land uses as infrastructure staging evolves.

Development in this sub-precinct is staged to align

with infrastructure delivery. A graduated approach

to the staging model is proposed, transitioning

from lighter industry near Cockle Creek to heavier

industrial and warehousing uses further within the

sub-precinct.

Early activation

is subject to geotechnical investigation and

confirmation that development will not

compromise TSF rehabilitation or increase societal

risk within the dam break inundation zone.

Killingworth

The northwest area near Killingworth presents

a strategic opportunity for land uses such as

advanced manufacturing, data-driven uses and

business parks, which take advantage of the

Transgrid substation and existing electricity

capacity. The area offers opportunity for local

uplift and diversification through enabling light

infrastructure, business parks, technology and

data-driven employment to support local jobs and

complement existing residential areas.

The sub-precinct is well-suited for activation given

its previously disturbed land provides a strong

foundation for redevelopment, complemented by

its proximity to existing high-voltage transmission

infrastructure and the Transgrid substation.

Additionally, road access is available via the

existing local road network, with potential for

future upgrades to support new land uses.

Water and wastewater servicing requires further

investigation. Bush fire and biodiversity interface

management will be required along the western

edge.

Barnsley West

Development of previously undisturbed areas

adjacent to existing residential in Barnsley is

contingent upon assessment of transmission

easements, servicing viability and biodiversity

values.

West Lake

The West Lake area offers excellent water quality

suitable for recreational use (subject to ongoing

monitoring). Rehabilitation around the lake has

been progressively signed off, with approximately

one-third approved and the balance targeted

for completion in 2026, indicating suitability for

recreational contact.

Existing walking tracks and connection

opportunities to Sugarloaf State Conservation

Area further enhance the Precinct’s potential for

tourism and recreation uses that are compatible

with the ecological and landscape values of the

area. Basic servicing for visitor amenities would be

required, while the western edge of the lake area

presents ecological constraints including

biodiversity corridors and remnant vegetation that

define the extent of any development boundaries.

Future development around the lake must

maintain water quality through appropriate

catchment management measures.

29

4  Structure plan and sub-precinct framework

### Page 30

Teralba

Teralba sub-precinct is strategically located

between the Teralba and Booragul train stations.

Proximity to existing utility networks reduces

servicing lead times and upfront infrastructure

costs. Established road access and adjacency

to nearby rail stations, residential communities

and employment areas provide a ready platform

for early development. Together, these attributes

present a compelling opportunity to deliver

residential outcomes that complement the

surrounding context and contribute to the

Precinct’s early activation and investment

momentum.

Medium-term activation

Medium-term activation areas require the delivery

of enabling infrastructure, resolution of key

transport and access constraints and progressive

risk reduction through ongoing rehabilitation and

technical investigations. These areas represent the

core employment-generating lands of the Precinct

and will require coordinated investment in roads,

utilities and potentially rail infrastructure.

Progressive development toward the southern and

more constrained areas will require coordinated

upgrades to transport, utilities and Precinct scale

water cycle management. This includes delivery of

wastewater infrastructure (currently absent across

much of the Precinct), expansion of water networks

and potential major electricity augmentation or

new substations where demand thresholds are

exceeded. Concurrently, transport upgrades,

including intersection capacity improvements,

new internal road links and potential additional

crossings of Cockle Creek, must be staged

alongside development to maintain network

performance and resilience.

Cockle Creek and Killingworth

residual land

Previously undisturbed areas outside the TSF and

dam break inundation zone with existing access to

the regional road network. Medium term activation

is subject to biodiversity investigations, geotechnical

investigation and flood risk assessment.

Medium term activation in Cockle Creek sub-

precinct requires confirmation that development

will not compromise TSF rehabilitation or increase

risk within the dam break inundation zone.

Long-term activation

Release of areas identified for long-term

development potential for productive use is

contingent upon the completion of critical

investigations, successful risk reduction through

ongoing rehabilitation and potentially major

infrastructure interventions.

Cockle Creek (TSF and dam break

inundation zone)

Development of the TSF area is contingent upon

several key prerequisites, including the completion

and regulatory acceptance of long-term dewatering

and stabilisation, together with an updated dam

break failure impact assessment reflecting current

capped conditions.

As a declared dam, development in both the TSF

and dam break inundation zone remain limited to

land uses that do not increase the risk to life or

undermine the structural stability of the TSF and

associated structures. The downstream dam break

inundation zone may be reduced in size over time

as rehabilitation progresses, potentially to the

point of revoking its declaration as a dam. Once

the TSF dam declaration is revoked, development

downstream of the dam can be achieved, subject to

other constraints.

Re-purposing and use of the TSF and associated

structures can occur provided detailed structural,

geotechnical and hydrological investigations occur

in parallel to each development application.

Until these prerequisites are met, the TSF and its

associated inundation zone may support interim

or ‘meanwhile’ uses that maintain a low population

level. Such interim uses could include solar energy

installations, for which international precedents on

tailings dams exist, as well as biodiversity corridor

functions, landscape rehabilitation and other low

occupancy uses.

Development within the further investigation areas

associated with the TSF and dam break inundation

areas may be brought forward to medium

horizon, either as a whole or in part, depending on

rehabilitation and ongoing monitoring.

30

4  Structure plan and sub-precinct framework

### Page 31

Staging triggers

The progressive release of developable land across

the Precinct is linked to the completion of key

technical investigations and the achievement of

rehabilitation milestones. The following staging

triggers apply as relevant across the Precinct:

•

Dam safety and Geotech – Geotechnical

monitoring and assessment of TSF, with the view

to de-declaring the dam. Updated dam break

and consequence assessments demonstrating

a reduction in the dam break inundation zone.

Refer to Section 9 Sustainability and resilience

on page 51 for detailed dam safety aims and

performance criteria.

•

Contamination – Completion of staged

contamination investigations and, where

required, remediation or management

measures appropriate to the proposed land

use, in accordance with the Contaminated Land

Management Act 1997 and State Environmental

Planning Policy (Resilience and Hazards) 2021.

•

Geotechnical stability – Geotechnical

assessments confirming the suitability of land

for the proposed development type, particularly

rehabilitated landforms.

•

Flooding – Detailed flood modelling confirming

flood planning levels, developable areas

and appropriate mitigation measures for

development within or adjacent to flood-

affected land, including climate change and

dam break interaction scenarios.

•

Infrastructure and servicing – Confirmation of

utility servicing capacity (water, wastewater,

electricity, telecommunications) and delivery

of enabling infrastructure to support

staged development. Refer to Section 10

Infrastructure, utilities and servicing on page

58 for detailed infrastructure and servicing

aims and performance criteria.

•

Biodiversity – Completion of detailed

environmental surveys to verify biodiversity

values and confirm environmentally constrained

area boundaries.

•

Take-up and market demand – Progressive

development is informed by demonstrated

market take-up across the Precinct.

The sequencing of development is to be

coordinated with the delivery of supporting

infrastructure to make sure that the transport

network, utilities and community facilities can

accommodate incremental growth. Development

staging should also be coordinated with mine

closure and rehabilitation activities so that land

use transformation proceeds in an orderly manner.

An indicative description of the staging triggers

according to sub-precincts is provided in Table 2.

31

4  Structure plan and sub-precinct framework

### Page 32

Table 2: Indicative staging triggers by sub-precinct

Sub

precinct

Timing

horizon

Staging intent

Key enabling triggers

Cockle

Creek

Short-

Medium-Long

Infrastructure-led and

staged development areas

linked to triggers

•

Completion of rehabilitation and Geotechnical verification

•

Adequate provision for site access (including heavy vehicle and rail

interface as required)

•

Delivery of enabling infrastructure and servicing

•

Detailed flood assessment in low-lying areas

•

Resolution of dam safety constraints (including reduction in dam break

inundation zone extent) relevant to the proposed development and site

access

•

Demonstrated market take-up of preceding stages within the sub-

precinct or across the Precinct.

Killingworth Short-Medium Infrastructure-led and

staged development areas

linked to triggers

•

Completion of rehabilitation and Geotechnical verification

•

Detailed flood modelling and confirmation of developable areas

•

Detailed flood assessment in low-lying areas

•

Assessment of biodiversity constraints to confirm developable land

•

Demonstrated market take-up of preceding stages within the sub-

precinct or across the Precinct.

West Lake

Short–

Medium

Infrastructure-led and

staged development areas

linked to triggers

•

Completion of rehabilitation and Geotechnical verification

•

Detailed flood assessment (including climate change and interaction

scenarios)

•

Delivery of enabling infrastructure and servicing (including consideration

of onsite servicing)

•

Assessment of biodiversity constraints to confirm developable land

•

Demonstrated market take-up of preceding stages within the sub-

precinct or across the Precinct.

Barnsley

West

Short–

Medium

Early to progressive

activation

•

Confirmation of servicing capacity

•

Local access upgrades

•

Verification of biodiversity and transmission easement constraints

•

Assessment and response to local constraints and management of

interface conditions with adjacent sensitive land uses

Teralba

Short

Early activation of

residential development

leveraging existing

infrastructure, transport

and adjoining centre

•

Completion of rehabilitation and Geotechnical verification

•

Completion of Detailed Site Investigation (DSI) and, where required,

Remedial Action Plan (RAP)

•

Confirmation of water and wastewater servicing capacity

32

4  Structure plan and sub-precinct framework

### Page 33

Desired future

character

The Precinct offers the

opportunity to deliver a

distinctive future character,

shaped by its post mining

landscape and a diverse mix

of land uses. Employment-

generating activity will anchor

the Precinct, complemented

by commercial, recreation,

community and visitor uses.

The Precinct will transform a legacy mining

landscape into the Lower Hunter’s leading post

mining employment precinct, becoming a well-

connected, productive and resilient destination

that is an attractive place to work, invest,

recreate and visit, with high-quality urban form

and integrated landscape.

5	 Built form and landscape

33

### Page 34

The following character principles guide Precinct development.

Built form

The Precinct supports employment generating development responsive to its

landscape context setting. Building orientation, scale and siting is carefully

considered to integrate with the site’s natural features.

Landscape

Building on existing high environmental value, the Precinct protects and

enhances its natural landscape, with remnant vegetation and waterways

treated as defining landscape elements that shape the Precinct’s character.

Biodiversity can be protected near development areas through the

establishment of green corridors, landscape buffers and setbacks that

respond to topography and ecological systems.

Place and identity

The Precinct offers the opportunity to create a distinctive identity that

reflects its natural qualities, cultural values and industrial history.

Public realm and mobility

Well-connected to surrounding networks, the site supports safe, clear

and legible movement systems that connect sub-precincts, support active

transport and prioritise pedestrian amenity and landscape integration at key

interfaces. Access and circulation are designed to respond to the scale of

employment uses.

Sustainability and resilience

Built form and landscape design embed water sensitive urban design

(WSUD), ecological restoration, efficient resource use and climate resilience,

delivering a precinct that performs as a productive landscape.

Interface and transition

Development at precinct edges manages the transition to environmentally

constrained areas and surrounding communities through graduated built

form, generous setbacks and landscape buffers that protect amenity and

maintain natural character.

Flexibility and staged activation

Built form and subdivision patterns accommodate staged delivery and

evolving uses over time, ensuring that interim conditions and early activation

areas contribute positively to precinct character without compromising long-

term outcomes.

34

5  Built form and landscape

### Page 35

Urban design and public realm

Urban design is guided by shift from mining to

employment-generating uses, as well as

opportunities for tourism and recreation. The

design approach prioritises functional, robust

and adaptable built form outcomes that support

a range of industrial, logistics and contemporary

employment uses.

Aims

•

Achieve high-quality urban design outcomes

consistent with the Better Placed (GANSW, 2017)

objectives.

•

Provide a mix of contemporary, high-quality

building types and sizes to support employment

opportunities that evolve in line with changing

economic drivers

•

Built form to be of high quality, with facades

that address the street and that have

articulation, modulation, passive surveillance

and street activation

•

Make sure building siting and scale respond to

landscape, context, environmental values and

interface conditions.

•

Strengthen precinct identity through landscape,

signage, landmarks and heritage-informed

placemaking.

•

Provide landscape setbacks and public realm

outcomes that support amenity, biodiversity and

movement.

•

Create an employment precinct, with well-

connected buildings, commercial nodes and

integrated public and active transport.

Performance criteria

A. Built form, subdivision patterns, open space

and interface treatments must respond to

rehabilitated landforms, engineered surfaces

and the post mining landscape character of the

Precinct.

B. Development must contribute to a coherent

precinct identity by integrating mining heritage,

landscape character and, where relevant,

Connecting with Country outcomes into built

form, landscape and material selection.

C. Buildings must respond to landscape character,

topography and interface conditions.

D. Building scale and height must respond to the

surrounding context, consider visual impact and

contribute to an appropriate variation in built

form character across the Precinct.

E. Road setbacks must incorporate landscape

treatments that strengthen precinct character

and support biodiversity and amenity outcomes.

F.	 Where existing structures are retained, adaptive

reuse must demonstrate compliance with

current safety and accessibility requirements.

G. Public domain, landscape and street design

must integrate WSUD assets to support urban

cooling, biodiversity, amenity and place identity.

Figure 23: Indicative industrial built form

development concept

Figure 24:  Indicative public realm development

concept

35

5  Built form and landscape

### Page 36

Sub-precinct interface consideration

The Precinct incorporates a range of contextual

interfaces, including environmentally constrained

areas, open space and recreation areas, and

external sensitive receivers such as established

residential communities. Three interface typologies

guide the design of the Precinct’s edges, each

shaped by the values of the adjoining land and

the role of the interface in protecting amenity,

biodiversity and bushfire safety outcomes:

•

Typology 1 – Development adjoining

environmentally constrained areas (including

heavily vegetated and bushfire-prone areas)

•

Typology 2 – Developable area to open space

and recreation areas

•

Typology 3 – Precinct boundary to external

context (including adjoining residential and

other sensitive receivers).

Each typology is illustrated separately in Figure 25

to Figure 27. Together, these treatments establish

high-quality, well-managed edges that retain

the values of adjoining land while supporting the

Precinct’s long-term productive use.

Aims

•

Establish clear, durable transitions between

developable areas, environmentally constrained

areas, open space and surrounding

communities.

•

Protect biodiversity values, ecological corridors,

waterways and cultural heritage from the

indirect effects of adjacent development,

including noise, light, dust, stormwater runoff,

weed invasion and uncontrolled access.

•

Provide that interface built form responds to the

scale, character and amenity of adjoining land.

•

Maintain permeability and connectivity

for people while managing access to

environmentally constrained areas.

Performance criteria

Typology 1 - Development adjoining

environmentally constrained areas

A. Development adjoining environmentally

constrained areas protects ecological values,

manages edge effects, accommodates bushfire

asset protection requirements and supports a

clear, maintainable boundary between urban and

conservation land.

B. A vegetated buffer planted with locally endemic

species must be provided to the environmentally

constrained areas, with a baseline width of 30

metres. This width may be reduced where a site-

specific ecological assessment demonstrates

that a narrower buffer will achieve equivalent or

improved ecological outcomes, having regard to

the sensitivity of the adjoining environmentally

constrained area.

C. Where a perimeter road provides the interface

between developable land and environmentally

constrained area, the road reserve may form part

of the buffer function.

D. The bushland side of any perimeter road must

be managed through bush regeneration to retain

endemic vegetation and ecological values. The

development side of the road must incorporate

low-maintenance bushfire asset protection

zones (e.g. wide road verges, managed grassed

verges) that integrate with the urban edge.

E. Buildings, hardstand, storage and operational

activities must not be located within the

ecological buffer or asset protection zone.

F.	 Development intensity at sensitive environmentally

constrained area interfaces is to be reduced

through setbacks, lower built form scale where

appropriate, and landscape screening to minimise

visual and ecological edge effects.

G. Lighting adjacent to environmentally constrained

areas is to be designed to minimise light spill,

glare and ecological disturbance to habitat areas.

H. Fencing at environmentally constrained

area interfaces must be in the form of a

maintainable barrier that controls access to the

environmentally constrained area while retaining

visual permeability where appropriate.

I.

Stormwater treatment measures must be located

within the developable area and outside riparian

buffers and environmentally constrained areas.

J.

Edge treatments must be designed to prevent

ongoing weed invasion into adjacent native

vegetation, including through selection of

non-invasive landscape species, ongoing

36

5  Built form and landscape

### Page 37

maintenance arrangements and clear physical

demarcation.

Typology 2 – Developable area to open space and

recreation areas

A.	 Development adjoining open space or recreation

areas must provide a positive, legible and active

interface to the public realm.

B.	 Pedestrian access points and landscape

treatments are to integrate seamlessly with

adjoining open space.

C.	 Buildings must be oriented to support Crime

Prevention Through Environmental Design

(CPTED) principles and provide passive

surveillance of public open space, where

appropriate to the proposed use.

D.	 Open space at sub-precinct interfaces are

to function as a connected system that links

environmentally constrained areas, walking and

cycling routes, significant vegetation and natural

landforms.

E.	 Lighting at open space interfaces must support

safe pedestrian movement while applying

CPTED and wildlife-friendly lighting principles

where the open space adjoins or connects to

environmentally constrained areas.

Typology 3 – Precinct boundary to external context

A.	 Development adjoining residential areas or other

sensitive receivers must provide setbacks and

landscape buffers informed by detailed land use

compatibility and acoustic assessment.

B.	 Buildings at sensitive interfaces must be

sited and designed to minimise overlooking,

overshadowing and visual dominance.

C.	 Acoustic, air quality and operational mitigation

measures must be incorporated where required

to manage amenity impacts.

D.	 Heavy vehicle access, loading and servicing

areas are not to be located at residential

interfaces unless no feasible alternative

is available and mitigation measures are

implemented to minimise noise, air quality and

amenity impacts.

E.	 Landscape screening must use locally

endemic species and contribute to amenity and

biodiversity outcomes.

F.	 Boundary interface treatments must respond

to the characteristics of the adjoining land,

including bushfire, ecological, riparian and

residential contexts.

Figure 25: Indicative interface concept – Typology 1 (Environmentally constrained areas)

37

5  Built form and landscape

### Page 38

Figure 26: Indicative interface concept – Typology 2 (Open space and recreation)

Figure 27: Indicative interface concept – Typology 3 (External context)

38

5  Built form and landscape

### Page 39

Biodiversity and habitat corridors

The Precinct consists of a combination of

previously disturbed land, rehabilitation areas and

undisturbed, remnant native bushland. Vegetation

includes existing cleared areas associated with the

historical operation of several former mine sites,

some of which have been rehabilitated back to

native bushland.

Aims

•

Protect areas of high biodiversity values from

development to avoid serious and irreversible

impacts on threatened ecological communities

and threatened species.

•

Promote a development outcome that is

consistent with the requirements of the avoid,

minimise and offset hierarchy of applicable

NSW and Commonwealth biodiversity

legislation.

•

Maintain the function of key linkages that

facilitate wildlife movement within the site and

the wider landscape.

•

Identify and secure environmentally constrained

land with an appropriate size and configuration

to be protected under suitable conservation

mechanisms.

•

Protect wetlands, watercourses, and associated

riparian corridors and aquatic habitats from

development.

•

Implement ecological restoration or

rehabilitation measures on residual land

or buffer zones to achieve a net positive

biodiversity outcome.

•

Apply ecologically sustainable development

principles for future land use and development.

•

Respond and adapt to future environmental

changes to avoid adverse impacts on high

biodiversity values.

Performance criteria

A. Development footprints must be located to avoid

and minimise impacts on areas of high

biodiversity values that could result in a serious

and irreversible impact on threatened ecological

communities or threatened species.

B. Development must avoid fragmentation of

existing key wildlife corridors as identified in the

draft Master Plan and must consider best-

practice species specific guidelines for future

corridor widths.

C. Development must apply Stage 1 and Stage 2

and associated detailed requirements of the

NSW Biodiversity Assessment Method for a

future biodiversity assessment where entry into

the NSW Biodiversity Offset Scheme is triggered.

D. Appropriate buffers and setbacks in accordance

with current applicable NSW and Commonwealth

guidelines must be provided to areas of high

biodiversity value to minimise indirect impacts

and future degradation.

E. Remnant native vegetation must be retained

where practicable and vegetation removal must

be avoided or minimised to maximise tree canopy

cover within a development precinct.

F. Development must incorporate suitable

mitigation measures for restoration or

rehabilitation of native vegetation communities

and associated habitats within residual land

or buffer zones that are enforced under a

Vegetation Management Plan.

G. Rehabilitation of native vegetation communities

and landscape planting must prioritise locally

endemic species and reflect the relevant plant

community types.

H. Development must avoid impacts to wetlands

and associated buffer zones where the wetland

provides important habitat for migratory

shorebirds.

I.

Development must avoid riparian areas and

should restore or rehabilitate the vegetated

riparian zone where practicable.

6	 Ecology, water and

landscape systems

39

### Page 40

Figure 28: High biodiversity values

40

6  Ecology, water and landscape systems

### Page 41

Water cycle management

Water cycle management is a key consideration

for future development within the Precinct. Diega

Creek and Cockle Creek are the two key waterways

located within the Precinct. Existing stormwater

management within the Precinct is through

natural flow paths within the undeveloped areas

and via water management infrastructure across

disturbed land. Water management infrastructure

includes catchment dams, sediment dams, storage

dams, spillways and drainage systems. Cockle

Creek is the main receiver of stormwater runoff

from the Precinct, receiving flows from upstream

tributaries, natural flow paths and water directed

from the disturbed areas via two licenced locations.

Aims

•

Adopt an integrated water cycle management

approach across the Precinct.

•

Minimise impacts on surface water, groundwater

and downstream receiving environments.

•

Incorporate WSUD to improve water quality,

resilience and place outcomes.

•

Maintain natural drainage function, groundwater

processes and recharge where feasible.

•

Manage construction-phase erosion and

sediment risks to protect sensitive receivers.

Performance criteria

A.	 Development must achieve applicable

stormwater quality targets, including pollutant

load reduction and nutrient load limits relevant

to the Lake Macquarie catchment.

B.	 High-priority groundwater dependent

ecosystems must be protected in accordance

with the applicable policy framework.

C.	 Development must demonstrate an integrated

water cycle and WSUD response that minimises

hydrological and water quality impacts on

downstream sensitive receivers.

D.	 WSUD measures must be designed to treat

frequent storm events, including flows up to and

including the three-month average recurrence

interval (ARI) event.

E.	 Development must maintain, to the extent

practicable, natural flow paths, sub-catchment

function and flow direction and must not rely

solely on piped or heavily engineered stormwater

systems where this would increase erosion,

scour or downstream impacts.

Figure 29: Concept for integrating water sensitive urban design

41

6  Ecology, water and landscape systems

### Page 42

Road network, freight and access

Road network and access is influenced by

the Precinct’s legacy as former coal mine

operations. Historic mining operations have shaped

both the physical terrain and created a framework

that continues to inform movement and access in

the post mining context. Former haul routes and

access tracks, originally designed to support

extraction, processing and transport activities,

establish a foundational spatial logic for the post

mining land use movement network.

The approach to managing transport and mobility is

multi-layered, combining infrastructure planning

and staging through demand management and

integration with land use outcomes. To facilitate

efficient movement within and around the Precinct,

the road network of sub-arterial, collector and local

roads is structured as a clear hierarchy, linking

developable land to the broader regional network

to minimise reliance on the external local network.

Subject to further investigation, a potential new

east–west crossing of Cockle Creek is identified as

an opportunity to strengthen network resilience,

unlock alternative freight access that bypasses

constrained local roads (Racecourse Road, Railway

Street and Rhondda Road) and improve

connectivity to Cockle Creek Station.

Teralba is directly serviced by Teralba and

Booragul Stations and forms a natural anchor for

enhanced pedestrian and cycling connectivity to

the wider Precinct via the Main Northern railway

corridor and the future active transport network.

Aims

•

Provide an efficient, legible and resilient road

network that supports sequenced Precinct

development.

•

Support safe and efficient freight, workforce

and visitor access to and within the Precinct.

•

Align freight and access planning with the

regional road and freight network, including

future strategic corridors.

•

Improve access across existing infrastructure

barriers, including the Main Northern Railway.

•

Integrate flood and bush fire resilience,

emergency access and network safety into road

planning.

•

Deliver complete streets that support walking,

cycling, buses and future transport upgrades.

Performance criteria

A. The Precinct road network must connect

to the regional road network and provide a

legible hierarchy of sub-arterial, collector and

local roads consistent with applicable design

standards.

B. Road network and intersection upgrades must

be delivered ahead of, or concurrently with, the

development stages they are intended to serve.

C. Internal road networks must be delivered

progressively to support sequenced

development and reduce reliance on external

local roads.

D. Development applications must demonstrate,

through detailed traffic assessment, that the

surrounding network and relevant intersections

can operate at an acceptable level of service for

the proposed stage of development.

E. Freight access routes and approved restricted

access vehicle (RAV) connections must be

established before freight-generating land uses

commence.

F.	 Heavy vehicle and freight movements must

avoid residential streets unless no feasible

alternative exists and acceptable mitigation is

demonstrated.

G. Former haul routes and access tracks should

be prioritised for long-term heavy vehicle

movements within and through the Precinct.

H. A freight management plan must be prepared

for freight-generating development and must

address internal freight circulation, last-mile

movements and community impact mitigation.

I.

Roads, intersections and bus facilities must be

designed to provide safe pedestrian access and

support public transport integration.

J.

Internal roads are to be located on developable

land and, where practical, within existing

7	 Transport and

connectivity

42

### Page 43

disturbed corridors, unless an alternative

alignment is required for safety or resilience

reasons.

K. Local road connections through the dam

break inundation zone must remain contingent

and must not be relied upon for development

until the relevant dam safety and suitability

requirements have been satisfied.

Figure 30: Potential transport network (short-term)

L. The Precinct’s road network, intersections, road

reserves must be designed to support efficient

and reliable public transport operations.

M. Parking must be provided in accordance with

an approved parking study and applicable

guidelines.

43

7  Transport and connectivity

### Page 44

Figure 31: Potential transport network (long-term)

44

7  Transport and connectivity

### Page 45

Figure 32: Future heavy vehicle network (short-term)

45

7  Transport and connectivity

## Page 11

Precinct constraints

The Precinct presents a range of environmental, physical and infrastructure

constraints that are managed through the structure plan and addressed

progressively through staged development and site-specific assessment at the

development application stage.

Geotechnical stability and risk management – Development on the TSF and the

land located in the dam break inundation zone to the north is currently limited.

Soft alluvial soils located around the coastal wetlands in the north of the site

influence construction methods.

Environmental – Existing areas of high biodiversity values, high bush fire risk

and flood affected areas require further investigation to inform development

siting and design.

Sensitive uses – Interfaces between existing land uses, including residential

receivers and potential future industrial land uses will need to be managed to

mitigate negative noise, odour and visual impacts.

Infrastructure – Heavy vehicle access to parts of the site is currently limited

due to steep gradients, access through local residential areas and existing rail

crossings. The location of the existing oil pipeline, electrical transmission lines

and their associated easements, setbacks and design measures will need to be

considered.

Utility infrastructure – Viability and sequencing of the provision of utilities,

particularly to the West Lake sub-precinct, will need further investigation.

11

2  Strategic context

-

## Page 12

Precinct vision

3	 Macquarie Coal

Complex Precinct

Figure 6: Vision: A new generational-scale employment precinct for the Hunter

12

## Page 13

Economic diversification and employment

•

A generational-scale opportunity to transform

former mining land into the Lower Hunter’s

premier employment precinct, delivering diverse

jobs and well-located employment land at a

regionally significant scale.

•

Enable a diversity of employment-generating

land uses that support regional economic

diversification, attract investment and create

local jobs.

•

A master planned, single-ownership Precinct

that attracts investment through flexible lot

configurations, co-location of complementary

industries and accommodation of large-footprint

uses.

•

A flexible, staged delivery framework that

aligns with mine closure commitments,

infrastructure capacity and changing economic,

social and market conditions, for the orderly

transformation from rehabilitation to productive

post mining uses.

Infrastructure and mobility

•

Leveraging existing transport connections to

deliver an efficient, well-serviced employment

precinct, with a legible internal road hierarchy

that supports safe and equitable access for

freight, workforce, public transport and active

transport users.

•

Utilities and services that meet the current

and future servicing needs of the Precinct,

whilst minimising land impacts and maximising

reliability, efficiency and sustainability.

Guiding principles

The guiding principles establish the Precinct-wide directions for land use, infrastructure, environmental

management, design quality and community benefit. They are to guide future planning, development

assessment, addenda to the draft Master Plan and staged implementation.

13

3  Macquarie Coal Complex Precinct

## Page 14

Environment and resilience

•

A connected network of high-value biodiversity,

wetlands and riparian corridors retained as

integral elements of the Precinct.

•

Encourage restorative and resilient development

that responds to biodiversity values, flood-prone

areas, drainage systems and minimises

cumulative impact.

•

Land use and development enable a coordinated

transformation to net-zero emissions.

•

A precinct-scale approach to managing post

mining constraints through a staged, risk-

informed framework that progressively develops

land as conditions mature.

•

Support circular economy models through

the co-location of complementary industries that

can share resources, infrastructure

and services, reducing waste and improving

resource efficiency.

Place and community benefits

•

A distinctive post mining landscape identity,

where rehabilitating landforms, remnant native

bushland, waterways and ecological corridors

shape the Precinct’s character and sense of

place.

•

High-quality urban design and public realm

outcomes with built form, subdivision

and interface treatments that respond to

topography, rehabilitated landforms and the

broader environmental and cultural setting.

•

Integrated community-supporting facilities co-

located with employment areas and public open

space, delivering tangible community and public

benefit at a scale that complements the

Precinct’s primary employment function.

•

Leveraging West Lake and environmentally

constrained areas to provide accessible

recreation, nature-based tourism and connected

trail and active transport network for workers,

surrounding communities and visitors.

14

3  Macquarie Coal Complex Precinct

## Page 15

mining land uses. It establishes the foundation for

planning, design and development to be guided by

the principles of the Government Architect NSW

Connecting with Country Framework.

As the draft Master Plan is exhibited and refined,

meaningful engagement with Lake Macquarie

Aboriginal community stakeholders will form

an important part of the process to refine and

finalise the draft Master Plan. This should include

engagement with Traditional Custodians, Aboriginal

knowledge holders, the Awabakal Local Aboriginal

Land Council, the Biraban Local Aboriginal Land

Council and other Aboriginal organisations or

representatives identified through the engagement

process.

Connecting with Country

The Precinct is located on Awabakal Country,

adjacent to the shores of Cockle Bay in the north

of Lake Macquarie. The draft Master Plan

recognises Country as a living system of

interconnected cultural, ecological and physical

relationships, including land, waters, skies, plants,

animals, cultural practices, stories and community.

It also recognises that planning for the

transformation of a former mining landscape must

be informed by an understanding of Country and

respectful engagement with Aboriginal people

who hold cultural knowledge, rights and

responsibilities for the area.

The draft Master Plan has been prepared as an

early framework for the transformation of the

Precinct from mining to sustainable and

productive post

Credit: Glencore

15

3  Macquarie Coal Complex Precinct

## Page 16

Structure plan

The structure plan (Figure 9) is the principal

spatial framework for the draft Master Plan. It

identifies the arrangement of developable areas,

environmentally constrained areas, recreational

areas, movement networks and key constraints

across the Precinct to guide development.

The structure plan outlines the spatial logic for

future development at a precinct scale, providing

a framework within which detailed design,

subdivision and development assessment will

occur. The structure plan is supported by technical

studies.

The following categories are used to describe land

within the structure plan:

•

Developable areas – Land that is potentially

suitable for development, subject to further

technical investigation and site-specific

assessment at the development application

stage.

•

Environmentally constrained areas – Land

identified as having biodiversity values or where

natural features (watercourses, wetlands, steep

slope, flooding) constrain development.

•

Recreation areas – Land potentially suitable for

active and passive recreation facilities,

balanced with protecting biodiversity and

cultural values.

•

Further investigation – Potentially developable

land that is constrained in the short to medium

term by geotechnical, dam safety, biodiversity

or flood risk factors, requiring resolution before

development can proceed. Development of this

land is contingent upon the completion

of relevant technical investigations and the

achievement of applicable staging triggers.

4	 Structure plan and

sub-precinct framework

Figure 7: Indicative visualisation east over

Macquarie Coal Complex Precinct

Figure 8: Indicative visualisation west over

Macquarie Coal Complex Precinct

16

## Page 17

Figure 9: Macquarie Coal Complex Precinct Structure Plan

17

4  Structure plan and sub-precinct framework

## Page 18

Sub-precinct framework

The structure plan organises the Precinct into

five development sub-precincts (Figure 10), set

within a connected network of environmentally

constrained areas that define the Precinct’s

landscape framework. Each sub-precinct presents

a distinctive opportunity, shaped by its topography,

legacy mining features, environmental values,

access and proximity to existing communities and

infrastructure.

Together the sub-precincts enable a coordinated,

staged transformation of the Precinct that

responds to physical setting while delivering

a diverse range of employment, recreation

and community outcomes. Each sub-precinct

description presents key characteristics, land use

intent and opportunities for future planning and

development, against which development proposals

will be assessed.

Figure 10: Sub-precincts

18

4  Structure plan and sub-precinct framework

## Page 19

Land use intent

Future development will be anchored by

employment-generating activity that supports

regional economic diversification, attracts

investment and creates local jobs. Complementary

commercial, recreation, community and visitor land

uses will support the workforce, deliver community

benefit and contribute to the broader public value

of the post mining tranformation.

Figure 11: Employment land use envisaged in the Precinct

Figure 12: Complementary land use typologies envisaged

19

4  Structure plan and sub-precinct framework

## Page 20

Cockle Creek

Characteristics

Cockle Creek sub-precinct is located in the eastern

portion of the Precinct and encompasses the

former MCPP, TSF, mine rail loop and associated

operational infrastructure. Its direct interface

with the Main Northern Railway, together with

established access from Racecourse Road,

Railway Street and The Weir Road, positions the

sub-precinct as a strategically connected gateway

within the broader Precinct.

Historic industrial use has shaped a substantially

modified landscape of previously disturbed land

and legacy infrastructure. These attributes provide

a strong foundation for early activation and support

the efficient reuse of land.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform a flexible,

opportunity-led planning response:

•

Reuse of legacy industrial assets – The former

coal preparation plant, mine rail loop and

existing rail interface with the Main Northern

railway provide a platform for new industrial,

manufacturing, energy and rail-related uses that

leverage available infrastructure.

•

Early activation of available land – Areas outside

the TSF and dam break inundation zone are well-

positioned for near-term development, with

further land progressively released as TSF

rehabilitation advances.

•

Enhanced connectivity – A potential new bridge

crossing of Cockle Creek is identified for

investigation to strengthen road access and

unlock additional development opportunities

across the sub-precinct.

•

Improved internal movement networks – New

internal road links will support integrated

movement across the sub-precinct, enabled by

revocation of the TSF dam declaration or

delivery of bridge infrastructure above the

inundation level.

•

Supporting industries that would facilitate rail

manufacturing, including workshops with skilled

trades.

•

Established access for short term activity

– Existing connections from Railway Street,

Racecourse Road, The Weir Road and Rhondda

Road provide immediate access to developable

land beyond the dam break inundation zone,

supporting early-stage uses.

•

Integration of environmental values – High value

biodiversity, fauna habitat and wetland areas to

north and east of the sub-precinct are retained

and integrated into the land use pattern,

supporting a considered balance between

development and environmental outcomes.

Figure 13: Indicative mixed industrial development

concept

Figure 14: Indicative mixed industrial

development concept utilising rail connectivity

20

4  Structure plan and sub-precinct framework

## Page 21

Killingworth

Characteristics

Killingworth sub-precinct is located in the north-

western portion of the Precinct, near established

residential areas of Killingworth and Barnsley.

Accessible topography, established road

connections via Wakefield Road and The Broadway,

and a direct interface with environmentally

constrained areas and biodiversity corridors to the

south and east define its place-based setting.

Its proximity to existing communities and the

prevalence of previously disturbed land from

former mining operations position the sub-precinct

as a strong candidate for early activation. These

attributes provide a practical platform for short-

term development opportunities, aligned with

rehabilitation outcomes and sequenced provision of

servicing.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-led

planning response:

•

Compatible community interface – Interface

with established residential areas of

Killingworth and Barnsley is managed through

appropriate buffers, setbacks and acoustic

treatments to make sure land use compatibility

and protect amenity.

•

Efficient access and movement – Accessible

topography and established connections

through Wakefield Road and The Broadway

enable efficient site access, with heavy vehicle

routing strategy that directs freight to approved

routes and reinforces the sub-precinct’s

logistics advantages.

•

Energy-enabled employment opportunity –

Proximity to the Transgrid substation positions

Killingworth to attract energy-intensive and

data-driven industries seeking reliable grid

access, supporting the Precinct’s role in the

Hunter’s energy and digital economy

transformation.

•

Local jobs – The sub-precinct’s location

adjoining established communities provides for

accessible local employment that supports

workforce participation and liveability across the

surrounding area.

•

Integration of environmental values – Interfaces

with environmentally constrained areas and

biodiversity corridors inform a considered land

use pattern that retains ecological connectivity

while enabling productive use of previously

disturbed land.

•

Evidence-based sequencing – Geotechnical,

water quality, utilities and access investigations

will inform the staged delivery of development.

Figure 15: Indicative light industrial development

concept

Figure 16: Indicative light industrial layout

development concept

21

4  Structure plan and sub-precinct framework

## Page 22

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-

led, planning response:

•

A landscape-led destination – West Lake will

evolve as the Precinct’s landscape, community

and visitor heart, where rehabilitated land, water

and bushland frame a curated employment,

tourism, recreation and interpretation concept

that supports economic diversification and long-

term adaptability.

•

Signature landscape setting and visitor

experience – The lake and distinctive landscape

identity that supports nature-based tourism,

recreation and visitor infrastructure, including

walking and cycling trails, lookouts, water-based

facilities and heritage interpretation.

•

Integrated landscape and environmental values

– Rehabilitation areas, habitat corridors and

interfaces with rural landscapes and

environmentally constrained areas inform a

considered land use pattern, with buffer zones

and edge treatments that protect surrounding

values and reinforce ecological connectivity

across the Precinct.

•

Evidence-based sequencing – Geotechnical,

water quality, utilities and access investigations

will inform the staged delivery of development.

West Lake

Characteristics

West Lake sub-precinct occupies the south-

western portion of the Precinct and encompasses

the former Westside void, now a

water-filled lake, together with the surrounding

rehabilitation areas. The sub-precinct’s distinctive

landscape identity is shaped by the interplay of

water, remnant bushland, rehabilitated landforms

and elevated topography, with expansive views

across the Precinct and towards Lake Macquarie.

The lake is a signature landscape asset that

anchors a unique sense of place. It provides

the foundation for nature-based experiences,

recreation and visitor infrastructure that enhance

the Precinct’s broader attractiveness as an

employment and lifestyle destination. The sub-

precinct enables an active waterfront approach

to commercial, tourism and recreation around the

foreshore, with development carefully integrated

to retain and showcase the area’s biodiversity and

landscape values.

Further investigation areas on the eastern side of

the lake offer additional opportunity for low-impact,

sensitive development that responds to the desired

future character of West Lake and complements its

biodiversity and landscape setting.

Figure 17: Indicative lakeside development concept

22

4  Structure plan and sub-precinct framework

## Page 23

Barnsley West

Characteristics

Barnsley West sub-precinct is in the north-western

portion of the Precinct, comprising separate parcels

of land associated with the former Wakefield

Colliery. Accessed via Wakefield Road and Charlton

Street, the sub-precinct sits within a distinctive

landscape setting shaped by its interface with

adjoining residential areas, environmentally

constrained lands and established transmission

infrastructure. High biodiversity land between

Barnsley West and the Killingworth sub-precinct

reinforces its discrete identity.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-

led, planning response:

•

Small-scale urban services and light industry

– The sub-precinct’s compact scale and

adjacency to residential areas provide for a

curated mix of small-scale urban services, light

industrial and complementary employment

uses that meet local needs while supporting the

Precinct’s broader economic diversification.

•

Amenity-led interface with Barnsley village –

The residential interface informs a high-quality

edge response, including built form transitions,

landscape buffers, acoustic treatments and

operational controls, that protect the amenity

and character of the existing community.

•

Coordinated infrastructure interface – Existing

transmission easements are integrated into

the land use pattern, informing layout, access

and development footprints that align with

infrastructure outcomes and unlock practical

development areas.

Figure 18: Indicative small unit industrial development concept

23

4  Structure plan and sub-precinct framework

## Page 24

Teralba

Characteristics

The Teralba sub-precinct is located approximately

two kilometres south-east of the main Precinct,

adjoining the established Teralba local centre. The

sub-precinct is defined by its direct proximity to

two rail stations, its interface with the heritage-

listed Teralba Conservation Area, and its integration

with the established residential and commercial

fabric of the Teralba village.

Together, these attributes position Teralba as the

Precinct’s mixed use sub-precinct, a compact,

well-serviced setting where new housing and

complementary uses can support the ongoing

vitality of the local centre and contribute to the

broader regional transformation envisaged by the

Master Plan.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-led

planning response:

•

Conveniently connected and serviced –

Positioned approximately 300 metres from

Booragul Station and 400 metres from Teralba

Station, the sub-precinct enables direct access

to the regional passenger rail network and

supports a walkable, low-car neighbourhood

model.

•

Reinforcement of the Teralba local centre –

Proximity to established retail, community and

commercial services provides the foundation

for residential and complementary uses that

strengthen the centre’s economic base, activate

the public realm and support day-to-day

amenity for residents and workers.

•

Heritage-informed place-making – The setting

of the Teralba Conservation Area and local

heritage items, including the Miner’s Cottages

and Teralba Public School, informs a considered

design response that respects established

character, scale and views, and integrates

heritage interpretation as a defining element of

local identity.

•

Landscape-led response to Cockle Creek – The

Cockle Creek corridor informs a considered

land use pattern that balances development

opportunity with waterway health, riparian

amenity and flood conveyance, delivering

a high-quality blue-green edge to the sub-

precinct.

•

Enhanced pedestrian and cycling connectivity

– New and upgraded active transport links

to Teralba Station and across the railway

strengthen the sub-precinct’s transit-oriented

potential and improve everyday connections

between the neighbourhood, the local centre

and surrounding communities.

•

Early activation potential – Progress in mine

closure and rehabilitation, together with

established servicing connections, proximity to

existing urban areas and direct public transport

access, positions the sub-precinct as a strong

candidate for early activation and near-term

delivery.

24

4  Structure plan and sub-precinct framework

## Page 25

Environmentally constrained areas

Characteristics

Environmentally constrained areas form an integral

and defining element of the Precinct’s structure,

comprising tracts of remnant native vegetation,

rehabilitation areas, riparian corridors, waterways

and ecological networks distributed across

the Precinct. Together, these areas establish a

connected environmental framework that supports

biodiversity, water cycle management, landscape

identity and Connecting with Country outcomes.

Environmentally constrained areas anchor the

structure plan in a high-quality landscape setting

and reinforce ecological connectivity across the

region. The intent of these lands is to protect and

enhance environmental, hydrological, cultural and

landscape values over the long-term, while

enabling sensitive land use where suitable.

Key opportunities

The following attributes shape the sub-precinct’s

development context and inform an opportunity-

led, planning response:

•

Anchoring the Precinct’s ecological framework

– High biodiversity areas, key fish habitat

and terrestrial corridors provide north–south and

east–west ecological connectivity across the

Precinct. Biodiversity corridors, coastal

wetlands, mapped waterways and areas subject

to Voluntary Conservation Agreements

informing a clear protection framework aligned

with statutory requirements.

•

Considered, evidence-based approach to

compatible use – Where supported by detailed

biodiversity assessment, low-impact, compatible

uses may be accommodated within these lands,

guided by the recognised hierarchy of avoid first,

minimise where avoidance is not practicable, and

offset residual impacts. This approach makes

sure that future use is sensitively located,

limited in scale, and consistent with the

retention and enhancement of biodiversity,

hydrological and landscape values.

•

Water cycle and landscape performance –

Riparian corridors along mapped waterways

provide for flood conveyance, stormwater

treatment and waterway health, contributing to

a resilient water cycle framework that supports

development outcomes elsewhere in the

Precinct.

•

Compatible low-impact recreation and visitor

experience – Walking trails, lookouts, nature-

based education and interpretation position the

environmentally constrained areas as part of a

layered land use framework that complements

community benefit and economic diversification

across the Precinct.

Figure 19: Indicative view of environmentally

constrained areas

Figure 20: Indicative trails within the environmentally

constrained areas

25

4  Structure plan and sub-precinct framework

## Page 26

Implementation and sequencing

Implementation

The implementation and delivery of the entire

Precinct vision is intended to be sequenced over

several decades, reflecting the need to manage

mine closure and rehabilitation responsibilities and

to allow the future land uses to evolve in alignment

with development uptake. Delivery of supporting

infrastructure is intended to be staged to correlate

with the development as it is implemented over

time.

Development sequencing provides for

infrastructure delivery that is proactive but demand

led and enables early activation while supporting

long-term, efficient and resilient precinct

development. Infrastructure delivery is to be

adaptive, demand driven and coordinated, ensuring

that development does not outpace enabling

infrastructure while maintaining flexibility for

market led uptake. Development is to be staged in

accordance with available infrastructure capacity,

with priority given to feasibility of connecting

with existing utilities and transport networks.

Infrastructure delivery should adopt an integrated

and coordinated approach across utilities and

transport to minimise disruption and duplication.

26

4  Structure plan and sub-precinct framework

## Page 27

Figure 21: Staging and key levers

27

4  Structure plan and sub-precinct framework

## Page 28

Development horizons

Development horizons are described in Table

Figure 22 illustrates the sequencing of

development within the Precinct, which reflects

the horizon within which land would commence

development, subject to the drivers and staging

triggers.

Table 1: Sub-precinct staging

Horizon

Timeframe

Key sub-precincts and drivers

Short-term

activation

0–5 years

Cockle Creek, Killingworth, West

Lake, Barnsley West, Teralba.

Medium-term

activation

5–15 years

Cockle Creek, Killingworth.

Long-term

activation

15+ years

Cockle Creek and Killingworth

residual land.

Figure 22: Sub-precinct staging

28

4  Structure plan and sub-precinct framework

## Page 29

Short-term activation

Areas identified as being capable of early release

for post mining land use development share

common characteristics, including land where

rehabilitation is at or near completion, existing

road access is available, servicing connections are

feasible and the risk profile is manageable without

requiring major investigations or infrastructure

upgrades.

Early phases are expected to leverage available

capacity within the Argenton Substation, existing

potable water connections and established regional

freight corridors, minimising the need for major

upfront augmentation. These areas also align with

transport accessibility and heavy vehicle routing

capability, supporting early industrial and logistics

uses.

These short-term activation areas provide the

opportunity to demonstrate viability of post mining

land use shift, generate investment confidence and

deliver tangible employment and community

outcomes.

Cockle Creek

Previously disturbed areas outside the TSF and

dam break inundation zone with existing access to

the regional road network. Early activation within

this sub-precinct could leverage the existing rail

loop with opportunities for related manufacturing

facilities.

This sub-precinct benefits from the strategic role

of freight and logistics in this area, leveraging

proximity to supporting flexible, freight-adjacent

land uses as infrastructure staging evolves.

Development in this sub-precinct is staged to align

with infrastructure delivery. A graduated approach

to the staging model is proposed, transitioning

from lighter industry near Cockle Creek to heavier

industrial and warehousing uses further within the

sub-precinct.

Early activation

is subject to geotechnical investigation and

confirmation that development will not

compromise TSF rehabilitation or increase societal

risk within the dam break inundation zone.

Killingworth

The northwest area near Killingworth presents

a strategic opportunity for land uses such as

advanced manufacturing, data-driven uses and

business parks, which take advantage of the

Transgrid substation and existing electricity

capacity. The area offers opportunity for local

uplift and diversification through enabling light

infrastructure, business parks, technology and

data-driven employment to support local jobs and

complement existing residential areas.

The sub-precinct is well-suited for activation given

its previously disturbed land provides a strong

foundation for redevelopment, complemented by

its proximity to existing high-voltage transmission

infrastructure and the Transgrid substation.

Additionally, road access is available via the

existing local road network, with potential for

future upgrades to support new land uses.

Water and wastewater servicing requires further

investigation. Bush fire and biodiversity interface

management will be required along the western

edge.

Barnsley West

Development of previously undisturbed areas

adjacent to existing residential in Barnsley is

contingent upon assessment of transmission

easements, servicing viability and biodiversity

values.

West Lake

The West Lake area offers excellent water quality

suitable for recreational use (subject to ongoing

monitoring). Rehabilitation around the lake has

been progressively signed off, with approximately

one-third approved and the balance targeted

for completion in 2026, indicating suitability for

recreational contact.

Existing walking tracks and connection

opportunities to Sugarloaf State Conservation

Area further enhance the Precinct’s potential for

tourism and recreation uses that are compatible

with the ecological and landscape values of the

area. Basic servicing for visitor amenities would be

required, while the western edge of the lake area

presents ecological constraints including

biodiversity corridors and remnant vegetation that

define the extent of any development boundaries.

Future development around the lake must

maintain water quality through appropriate

catchment management measures.

29

4  Structure plan and sub-precinct framework

## Page 30

Teralba

Teralba sub-precinct is strategically located

between the Teralba and Booragul train stations.

Proximity to existing utility networks reduces

servicing lead times and upfront infrastructure

costs. Established road access and adjacency

to nearby rail stations, residential communities

and employment areas provide a ready platform

for early development. Together, these attributes

present a compelling opportunity to deliver

residential outcomes that complement the

surrounding context and contribute to the

Precinct’s early activation and investment

momentum.

Medium-term activation

Medium-term activation areas require the delivery

of enabling infrastructure, resolution of key

transport and access constraints and progressive

risk reduction through ongoing rehabilitation and

technical investigations. These areas represent the

core employment-generating lands of the Precinct

and will require coordinated investment in roads,

utilities and potentially rail infrastructure.

Progressive development toward the southern and

more constrained areas will require coordinated

upgrades to transport, utilities and Precinct scale

water cycle management. This includes delivery of

wastewater infrastructure (currently absent across

much of the Precinct), expansion of water networks

and potential major electricity augmentation or

new substations where demand thresholds are

exceeded. Concurrently, transport upgrades,

including intersection capacity improvements,

new internal road links and potential additional

crossings of Cockle Creek, must be staged

alongside development to maintain network

performance and resilience.

Cockle Creek and Killingworth

residual land

Previously undisturbed areas outside the TSF and

dam break inundation zone with existing access to

the regional road network. Medium term activation

is subject to biodiversity investigations, geotechnical

investigation and flood risk assessment.

Medium term activation in Cockle Creek sub-

precinct requires confirmation that development

will not compromise TSF rehabilitation or increase

risk within the dam break inundation zone.

Long-term activation

Release of areas identified for long-term

development potential for productive use is

contingent upon the completion of critical

investigations, successful risk reduction through

ongoing rehabilitation and potentially major

infrastructure interventions.

Cockle Creek (TSF and dam break

inundation zone)

Development of the TSF area is contingent upon

several key prerequisites, including the completion

and regulatory acceptance of long-term dewatering

and stabilisation, together with an updated dam

break failure impact assessment reflecting current

capped conditions.

As a declared dam, development in both the TSF

and dam break inundation zone remain limited to

land uses that do not increase the risk to life or

undermine the structural stability of the TSF and

associated structures. The downstream dam break

inundation zone may be reduced in size over time

as rehabilitation progresses, potentially to the

point of revoking its declaration as a dam. Once

the TSF dam declaration is revoked, development

downstream of the dam can be achieved, subject to

other constraints.

Re-purposing and use of the TSF and associated

structures can occur provided detailed structural,

geotechnical and hydrological investigations occur

in parallel to each development application.

Until these prerequisites are met, the TSF and its

associated inundation zone may support interim

or ‘meanwhile’ uses that maintain a low population

level. Such interim uses could include solar energy

installations, for which international precedents on

tailings dams exist, as well as biodiversity corridor

functions, landscape rehabilitation and other low

occupancy uses.

Development within the further investigation areas

associated with the TSF and dam break inundation

areas may be brought forward to medium

horizon, either as a whole or in part, depending on

rehabilitation and ongoing monitoring.

30

4  Structure plan and sub-precinct framework

## Page 31

Staging triggers

The progressive release of developable land across

the Precinct is linked to the completion of key

technical investigations and the achievement of

rehabilitation milestones. The following staging

triggers apply as relevant across the Precinct:

•

Dam safety and Geotech – Geotechnical

monitoring and assessment of TSF, with the view

to de-declaring the dam. Updated dam break

and consequence assessments demonstrating

a reduction in the dam break inundation zone.

Refer to Section 9 Sustainability and resilience

on page 51 for detailed dam safety aims and

performance criteria.

•

Contamination – Completion of staged

contamination investigations and, where

required, remediation or management

measures appropriate to the proposed land

use, in accordance with the Contaminated Land

Management Act 1997 and State Environmental

Planning Policy (Resilience and Hazards) 2021.

•

Geotechnical stability – Geotechnical

assessments confirming the suitability of land

for the proposed development type, particularly

rehabilitated landforms.

•

Flooding – Detailed flood modelling confirming

flood planning levels, developable areas

and appropriate mitigation measures for

development within or adjacent to flood-

affected land, including climate change and

dam break interaction scenarios.

•

Infrastructure and servicing – Confirmation of

utility servicing capacity (water, wastewater,

electricity, telecommunications) and delivery

of enabling infrastructure to support

staged development. Refer to Section 10

Infrastructure, utilities and servicing on page

58 for detailed infrastructure and servicing

aims and performance criteria.

•

Biodiversity – Completion of detailed

environmental surveys to verify biodiversity

values and confirm environmentally constrained

area boundaries.

•

Take-up and market demand – Progressive

development is informed by demonstrated

market take-up across the Precinct.

The sequencing of development is to be

coordinated with the delivery of supporting

infrastructure to make sure that the transport

network, utilities and community facilities can

accommodate incremental growth. Development

staging should also be coordinated with mine

closure and rehabilitation activities so that land

use transformation proceeds in an orderly manner.

An indicative description of the staging triggers

according to sub-precincts is provided in Table 2.

31

4  Structure plan and sub-precinct framework

## Page 32

Table 2: Indicative staging triggers by sub-precinct

Sub

precinct

Timing

horizon

Staging intent

Key enabling triggers

Cockle

Creek

Short-

Medium-Long

Infrastructure-led and

staged development areas

linked to triggers

•

Completion of rehabilitation and Geotechnical verification

•

Adequate provision for site access (including heavy vehicle and rail

interface as required)

•

Delivery of enabling infrastructure and servicing

•

Detailed flood assessment in low-lying areas

•

Resolution of dam safety constraints (including reduction in dam break

inundation zone extent) relevant to the proposed development and site

access

•

Demonstrated market take-up of preceding stages within the sub-

precinct or across the Precinct.

Killingworth Short-Medium Infrastructure-led and

staged development areas

linked to triggers

•

Completion of rehabilitation and Geotechnical verification

•

Detailed flood modelling and confirmation of developable areas

•

Detailed flood assessment in low-lying areas

•

Assessment of biodiversity constraints to confirm developable land

•

Demonstrated market take-up of preceding stages within the sub-

precinct or across the Precinct.

West Lake

Short–

Medium

Infrastructure-led and

staged development areas

linked to triggers

•

Completion of rehabilitation and Geotechnical verification

•

Detailed flood assessment (including climate change and interaction

scenarios)

•

Delivery of enabling infrastructure and servicing (including consideration

of onsite servicing)

•

Assessment of biodiversity constraints to confirm developable land

•

Demonstrated market take-up of preceding stages within the sub-

precinct or across the Precinct.

Barnsley

West

Short–

Medium

Early to progressive

activation

•

Confirmation of servicing capacity

•

Local access upgrades

•

Verification of biodiversity and transmission easement constraints

•

Assessment and response to local constraints and management of

interface conditions with adjacent sensitive land uses

Teralba

Short

Early activation of

residential development

leveraging existing

infrastructure, transport

and adjoining centre

•

Completion of rehabilitation and Geotechnical verification

•

Completion of Detailed Site Investigation (DSI) and, where required,

Remedial Action Plan (RAP)

•

Confirmation of water and wastewater servicing capacity

32

4  Structure plan and sub-precinct framework

## Page 33

Desired future

character

The Precinct offers the

opportunity to deliver a

distinctive future character,

shaped by its post mining

landscape and a diverse mix

of land uses. Employment-

generating activity will anchor

the Precinct, complemented

by commercial, recreation,

community and visitor uses.

The Precinct will transform a legacy mining

landscape into the Lower Hunter’s leading post

mining employment precinct, becoming a well-

connected, productive and resilient destination

that is an attractive place to work, invest,

recreate and visit, with high-quality urban form

and integrated landscape.

5	 Built form and landscape

33

## Page 34

The following character principles guide Precinct development.

Built form

The Precinct supports employment generating development responsive to its

landscape context setting. Building orientation, scale and siting is carefully

considered to integrate with the site’s natural features.

Landscape

Building on existing high environmental value, the Precinct protects and

enhances its natural landscape, with remnant vegetation and waterways

treated as defining landscape elements that shape the Precinct’s character.

Biodiversity can be protected near development areas through the

establishment of green corridors, landscape buffers and setbacks that

respond to topography and ecological systems.

Place and identity

The Precinct offers the opportunity to create a distinctive identity that

reflects its natural qualities, cultural values and industrial history.

Public realm and mobility

Well-connected to surrounding networks, the site supports safe, clear

and legible movement systems that connect sub-precincts, support active

transport and prioritise pedestrian amenity and landscape integration at key

interfaces. Access and circulation are designed to respond to the scale of

employment uses.

Sustainability and resilience

Built form and landscape design embed water sensitive urban design

(WSUD), ecological restoration, efficient resource use and climate resilience,

delivering a precinct that performs as a productive landscape.

Interface and transition

Development at precinct edges manages the transition to environmentally

constrained areas and surrounding communities through graduated built

form, generous setbacks and landscape buffers that protect amenity and

maintain natural character.

Flexibility and staged activation

Built form and subdivision patterns accommodate staged delivery and

evolving uses over time, ensuring that interim conditions and early activation

areas contribute positively to precinct character without compromising long-

term outcomes.

34

5  Built form and landscape

## Page 35

Urban design and public realm

Urban design is guided by shift from mining to

employment-generating uses, as well as

opportunities for tourism and recreation. The

design approach prioritises functional, robust

and adaptable built form outcomes that support

a range of industrial, logistics and contemporary

employment uses.

Aims

•

Achieve high-quality urban design outcomes

consistent with the Better Placed (GANSW, 2017)

objectives.

•

Provide a mix of contemporary, high-quality

building types and sizes to support employment

opportunities that evolve in line with changing

economic drivers

•

Built form to be of high quality, with facades

that address the street and that have

articulation, modulation, passive surveillance

and street activation

•

Make sure building siting and scale respond to

landscape, context, environmental values and

interface conditions.

•

Strengthen precinct identity through landscape,

signage, landmarks and heritage-informed

placemaking.

•

Provide landscape setbacks and public realm

outcomes that support amenity, biodiversity and

movement.

•

Create an employment precinct, with well-

connected buildings, commercial nodes and

integrated public and active transport.

Performance criteria

A. Built form, subdivision patterns, open space

and interface treatments must respond to

rehabilitated landforms, engineered surfaces

and the post mining landscape character of the

Precinct.

B. Development must contribute to a coherent

precinct identity by integrating mining heritage,

landscape character and, where relevant,

Connecting with Country outcomes into built

form, landscape and material selection.

C. Buildings must respond to landscape character,

topography and interface conditions.

D. Building scale and height must respond to the

surrounding context, consider visual impact and

contribute to an appropriate variation in built

form character across the Precinct.

E. Road setbacks must incorporate landscape

treatments that strengthen precinct character

and support biodiversity and amenity outcomes.

F.	 Where existing structures are retained, adaptive

reuse must demonstrate compliance with

current safety and accessibility requirements.

G. Public domain, landscape and street design

must integrate WSUD assets to support urban

cooling, biodiversity, amenity and place identity.

Figure 23: Indicative industrial built form

development concept

Figure 24:  Indicative public realm development

concept

35

5  Built form and landscape

## Page 36

Sub-precinct interface consideration

The Precinct incorporates a range of contextual

interfaces, including environmentally constrained

areas, open space and recreation areas, and

external sensitive receivers such as established

residential communities. Three interface typologies

guide the design of the Precinct’s edges, each

shaped by the values of the adjoining land and

the role of the interface in protecting amenity,

biodiversity and bushfire safety outcomes:

•

Typology 1 – Development adjoining

environmentally constrained areas (including

heavily vegetated and bushfire-prone areas)

•

Typology 2 – Developable area to open space

and recreation areas

•

Typology 3 – Precinct boundary to external

context (including adjoining residential and

other sensitive receivers).

Each typology is illustrated separately in Figure 25

to Figure 27. Together, these treatments establish

high-quality, well-managed edges that retain

the values of adjoining land while supporting the

Precinct’s long-term productive use.

Aims

•

Establish clear, durable transitions between

developable areas, environmentally constrained

areas, open space and surrounding

communities.

•

Protect biodiversity values, ecological corridors,

waterways and cultural heritage from the

indirect effects of adjacent development,

including noise, light, dust, stormwater runoff,

weed invasion and uncontrolled access.

•

Provide that interface built form responds to the

scale, character and amenity of adjoining land.

•

Maintain permeability and connectivity

for people while managing access to

environmentally constrained areas.

Performance criteria

Typology 1 - Development adjoining

environmentally constrained areas

A. Development adjoining environmentally

constrained areas protects ecological values,

manages edge effects, accommodates bushfire

asset protection requirements and supports a

clear, maintainable boundary between urban and

conservation land.

B. A vegetated buffer planted with locally endemic

species must be provided to the environmentally

constrained areas, with a baseline width of 30

metres. This width may be reduced where a site-

specific ecological assessment demonstrates

that a narrower buffer will achieve equivalent or

improved ecological outcomes, having regard to

the sensitivity of the adjoining environmentally

constrained area.

C. Where a perimeter road provides the interface

between developable land and environmentally

constrained area, the road reserve may form part

of the buffer function.

D. The bushland side of any perimeter road must

be managed through bush regeneration to retain

endemic vegetation and ecological values. The

development side of the road must incorporate

low-maintenance bushfire asset protection

zones (e.g. wide road verges, managed grassed

verges) that integrate with the urban edge.

E. Buildings, hardstand, storage and operational

activities must not be located within the

ecological buffer or asset protection zone.

F.	 Development intensity at sensitive environmentally

constrained area interfaces is to be reduced

through setbacks, lower built form scale where

appropriate, and landscape screening to minimise

visual and ecological edge effects.

G. Lighting adjacent to environmentally constrained

areas is to be designed to minimise light spill,

glare and ecological disturbance to habitat areas.

H. Fencing at environmentally constrained

area interfaces must be in the form of a

maintainable barrier that controls access to the

environmentally constrained area while retaining

visual permeability where appropriate.

I.

Stormwater treatment measures must be located

within the developable area and outside riparian

buffers and environmentally constrained areas.

J.

Edge treatments must be designed to prevent

ongoing weed invasion into adjacent native

vegetation, including through selection of

non-invasive landscape species, ongoing

36

5  Built form and landscape

## Page 37

maintenance arrangements and clear physical

demarcation.

Typology 2 – Developable area to open space and

recreation areas

A.	 Development adjoining open space or recreation

areas must provide a positive, legible and active

interface to the public realm.

B.	 Pedestrian access points and landscape

treatments are to integrate seamlessly with

adjoining open space.

C.	 Buildings must be oriented to support Crime

Prevention Through Environmental Design

(CPTED) principles and provide passive

surveillance of public open space, where

appropriate to the proposed use.

D.	 Open space at sub-precinct interfaces are

to function as a connected system that links

environmentally constrained areas, walking and

cycling routes, significant vegetation and natural

landforms.

E.	 Lighting at open space interfaces must support

safe pedestrian movement while applying

CPTED and wildlife-friendly lighting principles

where the open space adjoins or connects to

environmentally constrained areas.

Typology 3 – Precinct boundary to external context

A.	 Development adjoining residential areas or other

sensitive receivers must provide setbacks and

landscape buffers informed by detailed land use

compatibility and acoustic assessment.

B.	 Buildings at sensitive interfaces must be

sited and designed to minimise overlooking,

overshadowing and visual dominance.

C.	 Acoustic, air quality and operational mitigation

measures must be incorporated where required

to manage amenity impacts.

D.	 Heavy vehicle access, loading and servicing

areas are not to be located at residential

interfaces unless no feasible alternative

is available and mitigation measures are

implemented to minimise noise, air quality and

amenity impacts.

E.	 Landscape screening must use locally

endemic species and contribute to amenity and

biodiversity outcomes.

F.	 Boundary interface treatments must respond

to the characteristics of the adjoining land,

including bushfire, ecological, riparian and

residential contexts.

Figure 25: Indicative interface concept – Typology 1 (Environmentally constrained areas)

37

5  Built form and landscape

## Page 38

Figure 26: Indicative interface concept – Typology 2 (Open space and recreation)

Figure 27: Indicative interface concept – Typology 3 (External context)

38

5  Built form and landscape

## Page 39

Biodiversity and habitat corridors

The Precinct consists of a combination of

previously disturbed land, rehabilitation areas and

undisturbed, remnant native bushland. Vegetation

includes existing cleared areas associated with the

historical operation of several former mine sites,

some of which have been rehabilitated back to

native bushland.

Aims

•

Protect areas of high biodiversity values from

development to avoid serious and irreversible

impacts on threatened ecological communities

and threatened species.

•

Promote a development outcome that is

consistent with the requirements of the avoid,

minimise and offset hierarchy of applicable

NSW and Commonwealth biodiversity

legislation.

•

Maintain the function of key linkages that

facilitate wildlife movement within the site and

the wider landscape.

•

Identify and secure environmentally constrained

land with an appropriate size and configuration

to be protected under suitable conservation

mechanisms.

•

Protect wetlands, watercourses, and associated

riparian corridors and aquatic habitats from

development.

•

Implement ecological restoration or

rehabilitation measures on residual land

or buffer zones to achieve a net positive

biodiversity outcome.

•

Apply ecologically sustainable development

principles for future land use and development.

•

Respond and adapt to future environmental

changes to avoid adverse impacts on high

biodiversity values.

Performance criteria

A. Development footprints must be located to avoid

and minimise impacts on areas of high

biodiversity values that could result in a serious

and irreversible impact on threatened ecological

communities or threatened species.

B. Development must avoid fragmentation of

existing key wildlife corridors as identified in the

draft Master Plan and must consider best-

practice species specific guidelines for future

corridor widths.

C. Development must apply Stage 1 and Stage 2

and associated detailed requirements of the

NSW Biodiversity Assessment Method for a

future biodiversity assessment where entry into

the NSW Biodiversity Offset Scheme is triggered.

D. Appropriate buffers and setbacks in accordance

with current applicable NSW and Commonwealth

guidelines must be provided to areas of high

biodiversity value to minimise indirect impacts

and future degradation.

E. Remnant native vegetation must be retained

where practicable and vegetation removal must

be avoided or minimised to maximise tree canopy

cover within a development precinct.

F. Development must incorporate suitable

mitigation measures for restoration or

rehabilitation of native vegetation communities

and associated habitats within residual land

or buffer zones that are enforced under a

Vegetation Management Plan.

G. Rehabilitation of native vegetation communities

and landscape planting must prioritise locally

endemic species and reflect the relevant plant

community types.

H. Development must avoid impacts to wetlands

and associated buffer zones where the wetland

provides important habitat for migratory

shorebirds.

I.

Development must avoid riparian areas and

should restore or rehabilitate the vegetated

riparian zone where practicable.

6	 Ecology, water and

landscape systems

39

## Page 40

Figure 28: High biodiversity values

40

6  Ecology, water and landscape systems

## Page 41

Water cycle management

Water cycle management is a key consideration

for future development within the Precinct. Diega

Creek and Cockle Creek are the two key waterways

located within the Precinct. Existing stormwater

management within the Precinct is through

natural flow paths within the undeveloped areas

and via water management infrastructure across

disturbed land. Water management infrastructure

includes catchment dams, sediment dams, storage

dams, spillways and drainage systems. Cockle

Creek is the main receiver of stormwater runoff

from the Precinct, receiving flows from upstream

tributaries, natural flow paths and water directed

from the disturbed areas via two licenced locations.

Aims

•

Adopt an integrated water cycle management

approach across the Precinct.

•

Minimise impacts on surface water, groundwater

and downstream receiving environments.

•

Incorporate WSUD to improve water quality,

resilience and place outcomes.

•

Maintain natural drainage function, groundwater

processes and recharge where feasible.

•

Manage construction-phase erosion and

sediment risks to protect sensitive receivers.

Performance criteria

A.	 Development must achieve applicable

stormwater quality targets, including pollutant

load reduction and nutrient load limits relevant

to the Lake Macquarie catchment.

B.	 High-priority groundwater dependent

ecosystems must be protected in accordance

with the applicable policy framework.

C.	 Development must demonstrate an integrated

water cycle and WSUD response that minimises

hydrological and water quality impacts on

downstream sensitive receivers.

D.	 WSUD measures must be designed to treat

frequent storm events, including flows up to and

including the three-month average recurrence

interval (ARI) event.

E.	 Development must maintain, to the extent

practicable, natural flow paths, sub-catchment

function and flow direction and must not rely

solely on piped or heavily engineered stormwater

systems where this would increase erosion,

scour or downstream impacts.

Figure 29: Concept for integrating water sensitive urban design

41

6  Ecology, water and landscape systems

## Page 42

Road network, freight and access

Road network and access is influenced by

the Precinct’s legacy as former coal mine

operations. Historic mining operations have shaped

both the physical terrain and created a framework

that continues to inform movement and access in

the post mining context. Former haul routes and

access tracks, originally designed to support

extraction, processing and transport activities,

establish a foundational spatial logic for the post

mining land use movement network.

The approach to managing transport and mobility is

multi-layered, combining infrastructure planning

and staging through demand management and

integration with land use outcomes. To facilitate

efficient movement within and around the Precinct,

the road network of sub-arterial, collector and local

roads is structured as a clear hierarchy, linking

developable land to the broader regional network

to minimise reliance on the external local network.

Subject to further investigation, a potential new

east–west crossing of Cockle Creek is identified as

an opportunity to strengthen network resilience,

unlock alternative freight access that bypasses

constrained local roads (Racecourse Road, Railway

Street and Rhondda Road) and improve

connectivity to Cockle Creek Station.

Teralba is directly serviced by Teralba and

Booragul Stations and forms a natural anchor for

enhanced pedestrian and cycling connectivity to

the wider Precinct via the Main Northern railway

corridor and the future active transport network.

Aims

•

Provide an efficient, legible and resilient road

network that supports sequenced Precinct

development.

•

Support safe and efficient freight, workforce

and visitor access to and within the Precinct.

•

Align freight and access planning with the

regional road and freight network, including

future strategic corridors.

•

Improve access across existing infrastructure

barriers, including the Main Northern Railway.

•

Integrate flood and bush fire resilience,

emergency access and network safety into road

planning.

•

Deliver complete streets that support walking,

cycling, buses and future transport upgrades.

Performance criteria

A. The Precinct road network must connect

to the regional road network and provide a

legible hierarchy of sub-arterial, collector and

local roads consistent with applicable design

standards.

B. Road network and intersection upgrades must

be delivered ahead of, or concurrently with, the

development stages they are intended to serve.

C. Internal road networks must be delivered

progressively to support sequenced

development and reduce reliance on external

local roads.

D. Development applications must demonstrate,

through detailed traffic assessment, that the

surrounding network and relevant intersections

can operate at an acceptable level of service for

the proposed stage of development.

E. Freight access routes and approved restricted

access vehicle (RAV) connections must be

established before freight-generating land uses

commence.

F.	 Heavy vehicle and freight movements must

avoid residential streets unless no feasible

alternative exists and acceptable mitigation is

demonstrated.

G. Former haul routes and access tracks should

be prioritised for long-term heavy vehicle

movements within and through the Precinct.

H. A freight management plan must be prepared

for freight-generating development and must

address internal freight circulation, last-mile

movements and community impact mitigation.

I.

Roads, intersections and bus facilities must be

designed to provide safe pedestrian access and

support public transport integration.

J.

Internal roads are to be located on developable

land and, where practical, within existing

7	 Transport and

connectivity

42

## Page 43

disturbed corridors, unless an alternative

alignment is required for safety or resilience

reasons.

K. Local road connections through the dam

break inundation zone must remain contingent

and must not be relied upon for development

until the relevant dam safety and suitability

requirements have been satisfied.

Figure 30: Potential transport network (short-term)

L. The Precinct’s road network, intersections, road

reserves must be designed to support efficient

and reliable public transport operations.

M. Parking must be provided in accordance with

an approved parking study and applicable

guidelines.

43

7  Transport and connectivity

## Page 44

Figure 31: Potential transport network (long-term)

44

7  Transport and connectivity

## Page 45

Figure 32: Future heavy vehicle network (short-term)

45

7  Transport and connectivity